USER’S MANUAL

PRELIMINARY

## LG Dynamic Braking Units

SV-DBU-U Series

LG Industrial Systems

LGIS constantly endeavors to improve its products so that information in this manual

is subject to change without notice.

Ver. 1.0  2001. 9

Overview

SV-DBU-U series is designed to use with LG inverter SV-iS5 and SV-iH series.

This manual describes the safety instructions that must be followed when installing, operating, and servicing. Read this manual completely before installing. The unit contains high voltage that can cause electric shock resulting in personal injury or loss of life.

Important User Information

Indicates that incorrect handling may cause

!  WARNING

!  CAUTION

!  WARNING

!  CAUTION

!  CAUTION

!  CAUTION

hazardous conditions, resulting in personal injury or

loss of life.

Indicates that incorrect handling may cause

physical damages.

"CAUTION" level instructions may lead to a serious result according to conditions.

Please follow the instructions of caution level for safety.

- Safety Instructions

- Electric Shock

- Do not open the front cover when the input power is introduced.

- Be sure to remove all input power from the braking unit including drive

before servicing.

- Wait at least 10 minutes before servicing and check the residual voltage.

- Service only qualified personnel.

- Fire

- Mount the braking unit and resistor on a non-flammable material.

Installing them on a flammable material may cause a fire.

- Do not connect the braking resistor directly to the DC terminal (P2, N) of

the drive. This can cause a fire.

- Injury

- Do not apply voltage to the terminals higher than the voltage specified in

the manual. This can cause damage and burst of the unit.

- Be sure to connect wires to the correct terminal. Especially, ensure the

polarity of DC power terminal. Otherwise, damage and burst of the unit

may occur.

- Do not touch the resistor right after the power is turned off. The resistor is still

hot.

- Other Instructions

- Do not operate the unit if enclosure damaged.

- Prevent any wire fragments, metallic particles from dropping during

installation.

- Nomenclature

-

SV

150

DBU

4U

| LG Drives | Symbol | Drive Capacity |  | Symbol | ## Type |  | Symbol | Drive Input Voltage |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 150 | 11~15[kW] |  | DBU | Dynamic Braking Unit |  | 2U | 200V Class |
|  | 220 | 18.5~22[kW] |  |  |  |  | 4U | 400V Class |
|  | 370 | 30~37[kW] |  |  |  |  |  |  |
|  | 550 | 45~55[kW] |  |  |  |  |  |  |
|  | 750 | 75[kW] |  |  |  |  |  |  |

- Specifications

  - 200V Class

| Type Spec. |  | SV150DBU -2U |  | SV220DBU -2U |  | SV370DBU -2U |  | SV550DBU -2U |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max. DC Input Voltage |  | # DC 400V |  |  |  |  |  |  |  |
| Applicable Drive Capacity [kW] |  | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55 |
| Braking Resistor | ### Wattage | 3.2 [KW] |  | 4.8 [KW] |  | 6.4 [KW] |  | 9.6 [KW] |  |
|  | Minimum Resistance | 8.5 [Ω] |  | 5.7 [Ω] |  | 4.2 [Ω] |  | 2.8 [Ω] |  |

  - 400V Class

| Type Spec. |  | SV150DBU-4U |  | SV220DBU-4U |  | SV370DBU-4U |  | SV550DBU-4U |  | SV750DBU-4U |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max. DC Input Voltage |  | # DC 800V |  |  |  |  |  |  |  |  |
| Applicable Drive Capacity |  | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55 | 75 |
| Braking Resistor | ### Wattage | 3.2 [KW] |  | 4.8 [KW] |  | 6.4 [KW] |  | 9.6 [KW] |  | 12.8 [kW] |
|  | Minimum Resistance | 8.5 [Ω] |  | 5.7 [Ω] |  | 4.2 [Ω] |  | 2.8 [Ω] |  | 8.4 [Ω] |

  - General Specifications

| Average Braking Torque |  | 100% |
| --- | --- | --- |
| Enable Duty |  | 10% (without cooling fan on heat sink) |
| Parallel Connection |  | Connectable up to 3 units in parallel |
| Maximum Turn On Time |  | 6 seconds |
| Output Signal |  | Heat Sink Overheat, Fuse Open, OC Trip |
| Protection |  | Heat Sink Overheat Protection, Over-Current Protection, Output Short Circuit Protection |
| Environmental Conditions | Operating Temperature | -10℃ ~ 40℃ |
|  | Humidity | Less Than 90 % RH Max. (Non-Condensing) |
|  | Altitude | 1,000m above sea level |
|  | Cooling Method | Natural Convection |
|  | Application Site | No Corrosive Gas, Combustible Gas, Oil Mist, or Dust |

- Installation

- Environmental Conditions

- Do not mount the unit in direct sunlight. Isolate the unit from excessive vibration.

- Protect the unit from moisture, dust, metallic particles, corrosive gases and liquids. Install the units on a non-flammable material and as smooth as possible.

- In case of installing many units in a panel, consider the air flows for power dissipation. (see below figures for proper installation)

DB Unit or

DB Resistor

DB Unit or

DB Resistor

DB Unit or

DB Resistor

GOOD                       BAD

<<Installing units in a panel>>

DB Unit or

DB Resistor

DB Unit or

DB Resistor

Cooling fan

DB Unit or

DB Resistor

DB Unit or

DB Resistor

Air flow

GOOD                            BAD

<<Fan location in a panel>>

- Mounting

The units must be mounted vertically with sufficient room (horizontally and vertically) from adjacent equipment.

SV-DBU

over 50mm

over 100mm

over100mm

over 50mm

- Terminal Configuration

- Power Terminals

G

B1

B2

N

P

| Terminal | Description |
| --- | --- |
| P | #### DC (+) input. Connect to “P2” or “P” terminal of drive |
| N | DC (-) input. Connect to “N” terminal of drive |
| G | #### Ground Terminal |
| B1 | Connect to braking resistor |
| B2 | Connect to braking resistor |

- Control Terminals

IN+

IN-

OUT+

OUT-

30B

30C

30A

| Terminal | Function |
| --- | --- |
| IN+ | Slave turn on signal input (when “Slave Mode” selected) |
| IN- | Slave turn on signal input (when “Slave Mode” selected) |
| OUT+ | Slave turn on signal output (when “Master Mode” selected) |
| OUT- | Slave turn on signal output (when “Master Mode” selected) |
| 30A | Fault signal output 30A : Normal open contact 30B : Normal close contact 30C : Common terminal |
| 30B |  |
| 30C |  |

(Refer to sec. 7 for details of Master/Slave Operation)

- Terminal Wiring

- The SV-iH series has two kinds of power terminal configurations. Make sure the wiring according to drive capacity.

- SV030iH-4, SV037iH-4, SV045iH-4, SV055iH-4 units do not provide terminals for DC reactor connection.

- Wiring Drive, DB unit and DB resistor

# DB Unit

P

N

G

B1

B2

Common bus bar

# Drive

P1

P2

B1

B2

DB Resistor

- Wiring Drive, DB unit, DB resistor and DC reactor

DB Unit

DB Resistor

P

N

G

B1

B2

B1

B2

P2

P1

Drive

DC Reactor

- Basic Wiring

1) Single Operation

MCCB

Drive

IM

Motor

R

U

Twist pair

S

V

전원

T

W

Twist pair

P1

B1

B2

B2

B1

5M max.

P2

P

TH1

N

30B

5M max.

G

G

30C

TH2

DB Unit

DB Resistor

* )  The SV030/037/045/055DBH-4 units provide only terminal “P” instead of terminal “P1” and “P2”. Please refer to “2) Wiring Drive, DB unit and DB resistor for SV030/037/045/055iH-4” for correct wiring.

- Use twist wire shorter than 10m between drive, DB unit and DB resistor.

- In case of master/slave operation, the control wire should be shorter than 2m with twist wire.

- Be sure to earth terminal “G” of drive and DB unit.

- Wire Size:

| DB Unit |  | Wire size |
| --- | --- | --- |
| 200V | SV150DBU-2U | 5.5㎟ |
|  | SV220DBU-2U | 8.0㎟ |
|  | SV370DBU-2U | 14.0㎟ |
|  | SV550DBU-2U | 14.0㎟ |
| 400V | SV150DBU-4U | 5.5㎟ |
|  | SV220DBU-4U | 5.5㎟ |
|  | SV370DBU-4U | 5.5㎟ |
|  | SV550DBU-4U | 8.0㎟ |
|  | SV750DBU-4U | 14.0㎟ |

- 7. Master / Slave Operation

- In case of parallel operation of two braking units, the one must be set at “Master” and the other at “Slave”. (When one braking unit is operated it must be set at “Master” : Factory default – “Master”)

- How to set to Master (on PCB)

- Set the “Select Switch JP1” as below figure.

SLAVE

MASTER

- How to set to Slave (on PCB)

- Set the “Select Switch JP1” as below figure.

SLAVE

MASTER

- Connection between Master and Slave

- Set one DB unit to “Master” and the other to “Slave”.

- Connect “OUT+” terminal of Master to “IN+” terminal of Slave and “OUT-”

terminal of Master to “IN-” terminal of Slave.

J13

OUT-

OUT+

IN-

IN+

OUT-

OUT+

IN-

IN+

J13

MASTER PCB

SLAVE PCB

2m max.

- Connecting 3 DB Units

- Set one DB unit to “Master” and others to “Slave”.

- Connect “OUT+” terminal of Master to “IN+” terminal of Slave and “OUT-”

terminal of Master to “IN-” terminal of Slave, respectively.

1m max.

OUT-

OUT-

OUT+

OUT+

MASTER PCB

SLAVE PCB1

IN-

IN-

J13

J13

IN+

IN+

OUT-

OUT+

IN-

IN+

J13

SLAVE PCB2

1m max.

- Master/Slave Operation

MCCB

Drive

R

U

IM

Motor

S

V

Input

Power

T

W

P1

B1

B2

B2

B1

5M max.

P2

P

N

TH1

OUT+

G

G

TH2

OUT-

MASTER DB Unit

EB Resistor

2M max.

5M max.

B1

B2

B2

B1

P

TH1

IN+

N

IN-

G

TH2

SLAVE DB Unit

DB Resistor

- Combination of DB Units according to Drive Capacity

- Combination of Braking Units

- 200V Class

| Applicable Drive [KW] | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Braking Unit | SV150DBU-2U |  | SV220DBU-2U |  | SV370DBU-2U |  | SV550DBU-2U |  |
| Braking Resistor | 3.2KW 8.5Ω |  | 4.8KW 5.7Ω |  | 6.4KW 4.2Ω |  | 9.6KW 2.8Ω |  |
| Applicable Motor [KW] | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55 |

- 400V Class

| Applicable Drive [KW] | 11 | 15 | 18.5 | 22 | 30 | 37 |
| --- | --- | --- | --- | --- | --- | --- |
| Braking Unit | SV150DBU-4U |  | SV220DBU-4U |  | SV370DBU-4U |  |
| Braking Resistor | 3.2KW 33.9Ω |  | 4.8KW 22.8Ω |  | 6.4KW 16.9Ω |  |
| Applicable Motor [KW] | 11 | 15 | 18.5 | 22 | 30 | 37 |

| Applicable Drive [KW] | 45 | 55 | 75 | 90 ~ 160 | 220 |
| --- | --- | --- | --- | --- | --- |
| Braking Unit | SV550DBU-4U |  | SV750DBU-4U | SV750DBU-4U * 2 EA | SV750DBU-4U * 3 EA |
| Braking Resistor | 9.6KW 11.4Ω |  | 12.8KW 8.4Ω | 12.8KW 8.4Ω * 2 EA | 12.8KW 8.4Ω * 3 EA |
| Applicable Motor [KW] | 45 | 55 | 75 | 90 ~ 160 | 220 |

- See below for the combination of DB Units and DB resistors.

- Combination of 200V Class Units

▶ Drive Capacity: 30[kW] ~ 37[kW]       ▶ Drive Capacity: 45[kW] ~ 55[kW]

SV037DBU-2U

4.2Ω, 6.4kW

DB

Resistor

DB Unit

Drive

Drive

SV037DBU-2U

SV037DBU-2U

DB

Resistor

DB

Resistor

DB Unit

DB Unit

4.2Ω, 6.4kW

4.2Ω, 6.4kW

- Combination of 400V Class Units

▶ Drive Capacity: 30[kW] ~ 37[kW]       ▶ Drive Capacity: 45[kW] ~ 75[kW]

SV037DBU-4U

16.9Ω, 6.4kW

DB

Resistor

DB Unit

Drive

Drive

SV075DBU-4U

DB

Resistor

DB

Resistor

DB Unit

16.9Ω, 6.4kW

16.9Ω, 6.4kW

▶ Drive Capacity: 90[kW] ~ 160[kW]

SV075DBU-4U

SV075DBU-4U

Drive

DB Unit

DB Unit

DB

Resistor

DB

Resistor

DB

Resistor

DB

Resistor

16.9Ω, 6.4kW

16.9Ω, 6.4kW

16.9Ω, 6.4kW

16.9Ω, 6.4kW

▶ Drive Capacity: 220[kW]

SV075DBU-4U

SV075DBU-4U

Drive

DB Unit

DB Unit

DB

Resistor

DB

Resistor

DB

Resistor

DB

Resistor

16.9Ω, 6.4kW

16.9Ω, 6.4kW

16.9Ω, 6.4kW

16.9Ω, 6.4kW

SV075DBU-4U

DB Unit

DB

Resistor

DB

Resistor

16.9Ω, 6.4kW

16.9Ω, 6.4kW

- Display LED and Fault Reset

The DB Unit have four LEDs on the frontcover. The green LEDs display main power input and braking operation. The red LEDs display fault status of the unit.

| Display | Function |
| --- | --- |
| POWER (RED) | This LED is turned on when the input power of the unit is introduced. |
| RUN (GREEN) | This LED is turned on when the unit is in the braking operation. |
| OHT (RED) | This LED is turned on and cut off (trip) the output when the heat sink of the unit is over heated. |
| OCT (RED) | This LED is turned on when an excessive current flows through the IGBT and the unit cut off the output to protect the unit. |
| FOT (RED) | This LED is turned on when the internal protective fuse is opened. |

- Dimensions

Units: [mm]