USER MANUAL

Fnet OPTION BOARD

SV-iS5 Series

Before Installing

This manual describes about the installation, operation, and precautions of Fnet board of iS5 series. Read the manual and precautions thoroughly before installation and operation. If not, it may cause break down of board and shorten the product life.

!  CAUTION

- Do not install the option board when the power is introduced. If not, both of the inverter and option board may be broke down. (Attach and detach the option board to the inverter control board after the capacitor discharged)

- ESD can cause break down of CMOS components. Do not touch the CMOS components without the board is grounded.

- Do not change the communication cable with the inverter power is turned on.

- Make sure to precisely insert the connector of inverter and option board

- Make sure the connection of signal wire (P, N). P signal wire must be connected to the P terminal.

- Connect terminal resistor at the last connected option board of 110 ohm, 1/2 watt. (refer to Figure 6)

- Check the parameter unit when setting the parameters.

1. Introduction

Fnet board provides control and monitoring of iS5 series inverter for GLOFA PLC via high-speed serial communication. The communication protocol is programmed with GLOFA PLC.

1.1. Benefits of using Fnet board

- It is possible to control the inverter with high-speed communication of 1M BPS.

- Easy installation and change of a system because the control and monitoring of inverter is accomplished by PLC programming.

- Multiple inverters can be connected only with 2 line wires, providing time saving and easy maintenance.

- Easy system integration by using PLC related devices.

1.2. Contents included

Fnet option consists 1 Fnet board, 2 connectors, 3 supporters, and manual.

2. Configuration and Installation

2.1.  Configuration

RX TX ERR OP

S P N S P N

Comm. Wire Terminal Block

Frame Ground

Figure 1. Board Configuration

2.1.1. Comm. Wire Terminal Blcok

S   P   N   S   P   N

Figure 2. Comm. Wire Terminal Blcok

| S | P | N |
| --- | --- | --- |
| Shield | Comm. Signal Wiring (P) | Comm. Signal Wiring (N) |

- * Two sets of “S”, “P”, “N” signal is connected in parallel respectively.
    * Connect terminal resistor at the last connected inverter between terminal P and N.

- (refer to Figure 6.)

- 2.1.2. Frame Ground

Frame Ground is connected to the ground of inverter.

2.1.3. Display LED

RX      TX     ERR    OP

Figure 3. Display LED

First Op LED starts flickering and Err LED, Tx LED, Rx LEDs flickers at interval of 250ms.

| - LED | - Description |  |
| --- | --- | --- |
| COM▶ Opt B/D 01 PLC-GF RXD | - ON during receiving |  |
| - TXD | - ON during transmitting |  |
| - ERR | - ON when there is frame error |  |
| - OP | - Normal operation | - Flickering by every 1 sec |
|  | - Fnet Comm. trouble | - Flickering by every 500 msec |
|  | - DPRAM trouble | - Flickering by every 2 sec |

2.2. Installing on Inverter Board

- Unscrew the crews that fasten the inverter board and install the copper supporters proveded.

- Install the Fnet board by inserting the connector of inverter and Fnet board and tighten the screws that unscrewed from the inverter board.

Figure 4. Installing Fnet board on Inverter board

3. System Configuration

FUEA Module







Inverter #1

Inverter #2

Inverter #N

Figure 5. Example of System Configuration

3.1.  Connection between PLC (FUEA) and Inverter (iS5)

Shield

P

N

Shield

P

N

INV-1

INV-2

FUEA(PLC)

Terminal R

110, 1/2W

Figure 6. Wiring

4. Comm. Specification

| Speed | 1 M bps |
| --- | --- |
| Method | Manchester Biphase-L, Frame Synchronous method |
| Comm. Cable | Twisted Pair Shielded Cable, Dedicated cable Cable Type: LIREV-AMESB 1 (PC 717 6705), Manufacturer: LG Cable |
| Node | Max. 64 per line |
| Length | Max. 750 m |
| Frame Format | Field Bus(IEC TC65 / SC65C / WG6 65C 90.8) |

5. Operating

5.1. Power On Test

Turn on the inverter power after installing the option boar, and then inverter perform Power On test.

5.2. Setting Inverter Parameter

Set inverter parameters described below using keypad.

5.2.1. Checking Option board [COM group/code# 01: PLC-GF]

This parameter checks the option board installed on inverter board. This code must

display “PLC-GF”.

5.2.2. Setting Inverter Number [COM group/code# 17:  0 ~ 63]

This parameter sets the station number of inverter. Inverter number must match

the station number set in PLC. Setting a same number at more than one inverter

cause communication error.

COM▶ Station ID

17             1

5.2.3. Setting Option Mode [COM group/code# 02]

Set the mode of Fnet board.

COM▶  Opt mode

02        None

- None
  Inverter is controlled by keypad or control terminal instead Fnet board.

- Command
  Inverter takes just run commands of Forward Run, Reverse Run, and Stop from the Fnet board.

- Freq
  Inverter takes just frequency command from the Fnet board.

- Cmd + Freq
  Inverter takes all commands from the Fnet board.

5.2.4. Setting Lost Command [I/O group/code# 48]

This parameter set the actions of inverter ahead when the communication is

disconnected (timeout) by some reasons such like DPRAM error, cable cutting.

I/O▶Lost command

48      None

<In case of “timeout” error >

- None: Inverter keeps the command that just have before the disconnection

of communication.

- FreeRun: Inverter stops with FreeRun (Coast to stop).

- Stop: Inverter stops with the deceleration ramp set at FU1 # 06.

5.2.5. Setting timeOut [I/O group/code# 49]
    This Parameter sets the time that inverter decides disconnection of communication.

Inverter takes actions of Lost Command after this set time.

I/O▶  Time out

49       1.0   sec

Default value is 1 second.

5.2.6. Precautions

- If the Lost Command(I/O #48) is set at “None”, inverter keeps running depends on the status of comm. Disconnection. This situation may cause serious accident in some cases. It is strongly recommended to set at “FreeRun” or “Stop” to prevent unexpected accident.

- Do not set the “timeout” less than the communication cycle between PLCand inverter.

- Do not use an inverter station ID number same as other device’s station ID. This may cause a conflict in the communication system.

6. Trouble shooting

If the communication function doesn’t work properly, check the status LED on Fnet voard as described below.

| Check point | LED status | Cause | Remedy |
| --- | --- | --- | --- |
| OP LED | No blinking | 1. Power connection failure 2. CPU error(defective) 3. LED error(defective) | 1. Check connection and power 2,3. Repair or change. |
|  | Blinking at 500ms cycle | Fnet communication error | Check connection (com. line) Check enable status of PLC |
|  | Blinking at 2sec. cycle | DPRAM error | Check connection with inverter Repair or change |
| ERR LED | ON | Damage due to noise | Check communication line Check noise source |
| TXD, RXD LED | TXD, RXD LED : OFF OP LED : blinking at 500ms cycle | No data exchange. | Check communication lie Check enable status of PLC |
|  | RXD, TXD LED : OFF OP LED : blinking at 500ms cycle | Wrong parameter set | Check inverter station ID is correct |
|  | RXD, TXD LED : ON OP LED : blinking at 1 sec. Motor : doesn’t run | Normality | Check set of #51 Opt mode of EXP group |

7. Parameter code (address is hexadecimal)

<Common area> : Available in all models regardless inverter rating

| Parameter address | Description | Unit | Read/ Write | Data value |
| --- | --- | --- | --- | --- |
| 0000 | Inverter type | - | R | 4: SV-iS5 |
| 0001 | Inverter capacity | - | R | 0: 0.75 1:1.5 2:2.2 3: 3.7 4: 5.5 5: 7.5 6: 11 7: 15 8: 18.5 9: 22 (220V class) 10: 0.75 11:1.5 12:2.2 13: 3.7 14: 5.5 15: 7.5 16: 11 17: 15 18: 18.5 19: 22(400V class) (Unit : kW) |
| 0002 | Input voltage | - | R | 0: 220V 1: 400/440V |
| 0003 | version | - | R | 0100: Ver. 1.00, 0101: Ver 1.01 |
| 0004 | Parameter change | - | R/W | 0: Not available(default) – N/A 1: Available |
| 0005 | Command freq. | 0.01 Hz | R/W | N/A |
| 0006 | Run command | - | R/W | N/A |
| 0007 | Accel. time | 0.1 sec | R/W |  |
| 0008 | Decel. Time | 0.1 sec | R/W |  |
| 0009 | Output current | 0.1 A | R |  |
| 000A | Output freq. | 0.01 Hz | R |  |
| 000B | Output voltage | 1 V | R |  |
| 000C | DC Link voltage | 1 V | R |  |
| 000D | Output power | 1 W | R |  |
| 000E | Operational status | - | R | Bit 0:Stop, Bit 1:Forward Bit 2:Reverse Bit 3:Fault(Trip) Bit 4:in Accel. Bit 5:in Decel. Bit 6:Reaching to target Bit 7:in DC Braking, Bit 8:in Stop Bit 9: Present direction Bit10: Brake open Bit13: Rem. Run/Stop Bit14: Rem. Freq. Cmd |
| Parameter address | Description | Unit | Read/Write | Data value |
| 000F | Trip information | - | R | Bit 0: OC, Bit 1: OV, Bit 2: EXT-A Bit 3: BX, Bit 4: LV, Bit 5: Fuse Open, Bit 6: GF Bit 7: OH, Bit 8: ETH, Bit 9: OLT Bit 10: HW-Diag Bit 11:EXT-B Bit 12:ASHT Bit 13:OPT Bit 14:PO Bit 15:IOLT |
| 0010 | Input terminal information | - | R | Bit 0: FX, Bit 1: RX, Bit 2: BX Bit 3: RST,- Bit 8: P1, Bit 9: P2, Bit 10: P3 Bit 11: P4, Bit 12: P5, Bit 13: P6 |
| 0011 | Output terminal information | - | R | Bit 0: Q1 (OC1) , Bit 1: Q2 (OC2) Bit 2: Q3 (OC3), Bit 3: AUX |
| 0012 | V1 | - | R | 0 – FFFF |
| 0013 | V2 | - | - |  |
| 0014 | I | - | R | 0 – FFFF |
| 0015 | RPM | - | R |  |
| 0016 | Run command(Option)( Note 1) | 0.01Hz | R/W | Bit 0:Stop, Bit 1:Forward Bit 2:Reverse Bit 3:Fault reset Bit 4:Emergency stop |
| 0017 | Command freq. (Option) | 0.01Hz | R/W | 0 – 60000 |
| 0018 | Slip freq.(Option) | 0.01Hz | R/W | 0 – 60000 |
| 0019 | Ramp Freq.(Option) | 0.01Hz | R/W | 0 – 60000 |

(Note1) * Run command is activating when 0 is triggered to 1.
      * Run command 0 set makes “stop”.

(Note 2) Parameter changed in common area can not be stored. The modified parameter is available during the present operation but it is not valid after the power of disconnection or reset. It returns to default value. The parameter changed in other groups is valid until it is changed to new.
< DRV Group >

| Address | No. | Description | Default | Max. value | Min. value | Unit |
| --- | --- | --- | --- | --- | --- | --- |
| 5100 | DRV#00 | Cmd. Freq. | 0 | max freq. | Start freq. | 0.01Hz |
| 5101 | DRV#01 | Acc. Time | 50 | 60000 | 0 | 0.01sec |
| 5102 | DRV#02 | Dec. Time | 100 | 60000 | 0 | 0.01sec |
| 5103 | DRV#03 | Drive mode | 1 | 2 | 0 |  |
| 5104 | DRV#04 | Freq. mode | 0 | 4 | 0 |  |
| 5105 | DRV#05 | Step freq - 1 | 1000 | MaxFreq | startFreq | 0.01Hz |
| 5106 | DRV#06 | Step freq - 2 | 2000 | MaxFreq | startFreq | 0.01Hz |
| 5107 | DRV#07 | Step freq - 3 | 3000 | MaxFreq | startFreq | 0.01Hz |
| 510A | DRV#10 | DC Link Voltage | 0 | - | - | V |

< FU1 Group >

| Address | No. | Desciption | Default | Max. value | Min. value | Unit |
| --- | --- | --- | --- | --- | --- | --- |
| 5201 | FU1 #01 | Drive mode | 1 | 2 | 0 |  |
| 5202 | FU1 #02 | Freq. mode | 0 | 4 | 0 |  |
| 5203 | FU1 #03 | Run prohibit | 0 | 2 | 0 |  |
| 5205 | FU1 #05 | Acc. pattern | 0 | 4 | 0 |  |
| 5206 | FU1 #06 | Dec. pattern | 0 | 4 | 0 |  |
| 5207 | FU1 #07 | Stop mode | 0 | 2 | 0 |  |
| 5208 | FU1 #08 | DcBr freq. | 500 | 6000 | startFreq | 0.01Hz |
| 5209 | FU1 #09 | DcBlk time | 10 | 6000 | 0 | 0.01sec |
| 520A | FU1 #10 | DcBr value | 50 | 1000 | 0 | 0.1% |
| 520B | FU1 #11 | DcBr time | 10 | 600 | 0 | 0.1sec |
| 520C | FU1 #12 | DcSt value | 50 | 1000 | 0 | 0.1% |
| 520D | FU1 #13 | DcSt time | 0 | 600 | 0 | 0.1sec |
| 5214 | FU1 #20 | Max freq. | 6000 | 40000 | 4000 | 0.01Hz |
| 5215 | FU1 #21 | Base freq. | 6000 | maxFreq | 3000 | 0.01Hz |
| 5216 | FU1 #22 | Start freq. | 50 | 1000 | 10 | 0.01Hz |
| 5217 | FU1 #23 | Freq limit | 0 | 1 | 0 |  |
| 5218 | FU1 #24 | F-limit Lo. | 0 | highFreq | startFreq | 0.01Hz |
| 5219 | FU1 #25 | F-limit Hi. | 6000 | maxFreq | lowFreq | 0.01Hz |
| 521A | FU1 #26 | Torque boost | 0 | 1 | 0 |  |
| 521B | FU1 #27 | Fwd boost | 20 | 200 | 0 | 0.1% |
| 521C | FU1 #28 | Rev boost | 20 | 200 | 0 | 0.1% |
| 521D | FU1 #29 | V/F pattern | 0 | 2 | 0 |  |
| 521E | FU1 #30 | User freq. 1 | 1500 | maxFreq | 0 | 0.01Hz |
| 521F | FU1 #31 | User volt. 1 | 25 | 100 | 0 | % |
| 5220 | FU1 #32 | User freq. 2 | 3000 | maxFreq | 0 | 0.01Hz |
| 5221 | FU1 #33 | User volt. 2 | 50 | 100 | 0 | % |
| 5222 | FU1 #34 | User freq. 3 | 4500 | maxFreq | 0 | 0.01Hz |
| 5223 | FU1 #35 | User volt. 3 | 75 | 100 | 0 | % |
| 5224 | FU1 #36 | User freq. 4 | 6500 | maxFreq | 0 | 0.01Hz |
| 5225 | FU1 #37 | User volt. 4 | 100 | 100 | 0 | % |
| 5226 | FU1 #38 | Volt control | 100 | 110 | 40 | % |
| 5227 | FU1 #39 | Energy save | 0 | 80 | 0 | % |
| 5232 | FU1 #50 | ETH select | 0 | 1 | 0 |  |
| 5233 | FU1 #51 | ETH 1min | 150 | 200 | contPerc | % |
| 5234 | FU1 #52 | ETH Cont | 100 | 150 | 50 | % |
| 5235 | FU1 #53 | Motor type | 0 | 1 | 0 |  |
| 5236 | FU1 #54 | OL level | 150 | 150 | 30 | % |
| 5237 | FU1 #55 | OL time | 100 | 300 | 0 | 0.1sec |
| 5238 | FU1 #56 | OLT select | 0 | 1 | 0 |  |
| 5239 | FU1 #57 | OLT level | 180 | 200 | 30 | % |
| 523A | FU1 #58 | OLT time | 600 | 60000 | 0 | 0.1sec |
| 523B | FU1 #59 | Stall prev. | 0 | 7 | 0 |  |
| 523C | FU1 #60 | Stall level | 150 | 150 | 30 | % |

< FU2 Group >

| Address | No. | Description | Default | Max. Value | Min.Value | Unit |
| --- | --- | --- | --- | --- | --- | --- |
| 530A | FU2 #10 | Jump freq | 0 | 1 | 0 |  |
| 530B | FU2 #11 | jump lo 1 | 1000 | jump Hi 1 | StartFreq | 0.01Hz |
| 530C | FU2#12 | jump Hi 1 | 1500 | maxFreq | jump Lo 1 | 0.01Hz |
| 530D | FU2 #13 | jump lo 2 | 2000 | jump Hi 2 | StartFreq | 0.01Hz |
| 530E | FU2 #14 | jump Hi 2 | 2500 | maxFreq | jump Lo 2 | 0.01Hz |
| 530F | FU2 #15 | jump lo 3 | 3000 | jump Hi 3 | startFreq | 0.01Hz |
| 5310 | FU2 #16 | jump Hi 3 | 3500 | maxFreq | jump Lo 3 | 0.01Hz |
| 5314 | FU2 #20 | Power-on run | 0 | 1 | 0 |  |
| 5315 | FU2 #21 | RST restart | 0 | 1 | 0 |  |
| 5316 | FU2 #22 | Speed Search | 0 | 15 | 0 |  |
| 5317 | FU2 #23 | SS Sup-Curr | 100 | 200 | 80 |  |
| 5318 | FU2 #24 | SS P-gain | 1000 | 30000 | 0 |  |
| 5319 | FU2 #25 | SS I-gain | 10000 | 30000 | 0 |  |
| 531A | FU2 #26 | Retry number | 0 | 10 | 0 |  |
| 531B | FU2 #27 | Retry delay | 10 | 600 | 0 | 0.1sec |
| 531E | FU2#30 | Motor select | 0 | 9 | 0 |  |
| 531F | FU2#31 | Pole number | 4 | 12 | 2 |  |
| 5320 | FU2 #32 | Rated-Slip | 200 | 1000 | 0 | 0.01Hz |
| 5321 | FU2 #33 | Rated-Curr | 18 | 2000 | 10 | 0.1A |
| 5322 | FU2 #34 | Noload-Curr | 7 | 2000 | 5 | 0.1A |
| 5324 | FU2 #36 | Efficiency | 72 | 100 | 70 |  |
| 5327 | FU2 #39 | Carrier freq | 50 | 150 | 10 | 0.1kHZ |
| 5328 | FU2 #40 | Control mode | 0 | 3 | 0 |  |
| 5329 | FU2 #41 | Auto tuning | 0 | 1 | 0 |  |
| 532A | FU2 #42 | Rs | 0 | 5000 ( Note 3) | 0 | 0.001ohm |
| 532B | FU2 #43 | Rr | 0 | 5000 ( Note 4) | 0 | 0.001ohm |
| 532C | FU2 #44 | Lsigma | 0 | MaxInduc (Note 5) | 0 | 0.001mH |
| 5332 | FU2 #50 | PID F/B | 0 | 2 | 0 |  |
| 5333 | FU2 #51 | PID P-gain | 3000 | 30000 | 0 |  |
| 5334 | FU2 #52 | PID I-time | 300 | 30000 | 0 |  |
| 5335 | FU2 #53 | PID D-time | 1 | 30000 | 0 |  |
| 5336 | FU2 #54 | PID limit | 6000 | maxFreq | StartFreq | 0.01Hz |
| 5346 | FU2 #70 | Acc/Dec freq | 0 | 1 | 0 |  |
| 5347 | FU2 #71 | Time scale | 1 | 2 | 0 |  |
| 5348 | FU2 #72 | PowerOn disp | 0 | 6 | 0 |  |
| 5349 | FU2 #73 | User disp | 0 | 2 | 0 |  |
| 534A | FU2 #74 | RPM factor | 100 | 200 | 1 | % |
| 534B | FU2 #75 | DB mode | 1 | 2 | 0 |  |
| 534C | FU2 #76 | DB %ED | 10 | 30 | 0 | % |
| 534F | FU2 #79 | S/W Version |  |  |  |  |
| 5351 | FU2 #81 | 2nd Acc time | 50 | 60000 | 0 | 0.01sec |
| 5352 | FU2 #82 | 2nd Dec time | 100 | 60000 | 0 | 0.01sec |
| 5353 | FU2 #83 | 2nd BaseFreq | 6000 | maxFreq | 3000 | 0.01Hz |
| 5354 | FU2 #84 | 2nd V/F | 0 | 2 | 0 |  |
| 5355 | FU2 #85 | 2nd F-boost | 20 | 200 | 0 | 0.1% |
| 5356 | FU2 #86 | 2nd R-boost | 20 | 200 | 0 | 0.1% |
| 5357 | FU2 #87 | 2nd Stall | 150 | 150 | 30 | % |
| 5358 | FU2 #88 | 2nd ETH 1min | 150 | 200 | 2nd ETH Cont | % |
| 5359 | FU2 #89 | 2nd ETH Cont. | 100 | 2nd ETH 1min | 50 | % |
| 535A | FU2 #90 | 2nd R-Curr | 36 | 2000 | 10 | 0.1A |
| 538D | FU2 #93 | Para. init | 0 | 6 | 0 |  |

(Note 3,4,5) The values are vary for the motor ratings.

< I/O Group >

| Address | No | Description | Default | Max. value | Min.value | Unit |
| --- | --- | --- | --- | --- | --- | --- |
| 5401 | I/O #01 | V1 filter | 10 | 10000 | 0 | ms |
| 5402 | I/O #02 | V1 volt x1 | 0 | V1 vort x2 | 0 | 0.01V |
| 5403 | I/O #03 | V1 freq y1 | 0 | maxFreq | 0 | 0.01Hz |
| 5404 | I/O #04 | V1 volt x2 | 1000 | 1000 | V1 volt x1 | 0.01V |
| 5405 | I/O #05 | V1 freq y2 | 6000 | maxFreq | 0 | 0.01Hz |
| 5406 | I/O #06 | I filter | 10 | 10000 | 0 | ms |
| 5407 | I/O #07 | I curr x1 | 0 | I curr x2 | 0 | 0.01mA |
| 5408 | I/O #08 | I freq y1 | 0 | maxFreq | 0 | 0.01Hz |
| 5409 | I/O #09 | I curr x2 | 2000 | 2000 | I curr x1 | 0.01mA |
| 540A | I/O #10 | I freq y2 | 6000 | maxFreq | 0 | 0.01Hz |
| 540B | I/O #11 | Wire broken | 0 | 2 | 0 |  |
| 540C | I/O #12 | P1 define | 0 | 25 | 0 |  |
| 540D | I/O #13 | P2 define | 1 | 25 | 0 |  |
| 540E | I/O #14 | P3 define | 2 | 25 | 0 |  |
| 540F | I/O #15 | In Status | 0 | 1 | 0 |  |
| 5410 | I/O #16 | Out Status | 0 | 1 | 0 |  |
| 5411 | I/O #17 | Ti Filt Num | 15 | 50 | 2 |  |
| 5414 | I/O #20 | Jog freq | 1000 | MaxFreq | startFreq | 0.01Hz |
| 5418 | I/O #24 | Step freq - 4 | 4000 | MaxFreq | startFreq | 0.01Hz |
| 5419 | I/O #25 | Step freq - 5 | 5000 | MaxFreq | startFreq | 0.01Hz |
| 541A | I/O #26 | Step freq - 6 | 4000 | MaxFreq | startFreq | 0.01Hz |
| 541B | I/O #27 | Step freq - 7 | 3000 | MaxFreq | startFreq | 0.01Hz |
| 541E | I/O #30 | Acc time– 1 | 200 | 60000 | 0 | 0.1sec |
| 541F | I/O #31 | Dec time – 1 | 200 | 60000 | 0 | 0.1sec |
| 5420 | I/O #32 | Acc time – 2 | 300 | 60000 | 0 | 0.1sec |
| 5421 | I/O #33 | Dec time – 2 | 300 | 60000 | 0 | 0.1sec |
| 5422 | I/O #34 | Acc time – 3 | 400 | 60000 | 0 | 0.1sec |
| 5423 | I/O #35 | Dec time - 3 | 400 | 60000 | 0 | 0.1sec |
| 5428 | I/O #40 | FM mode | 0 | 3 | 0 |  |
| 5429 | I/O #41 | FM adjust | 100 | 400 | 10 | % |
| 542A | I/O #42 | FDT freq | 3000 | maxFreq | 0 | 0.01Hz |
| 542B | I/O #43 | FDT band | 1000 | maxFreq | 0 | 0.01Hz |
| 542C | I/O #44 | Aux mode | 12 | 18 | 0 |  |
| 542D | I/O #45 | Relay mode | 2 | 7 | 0 | BIT3 |
| 542E | I/O #46 | Inv No. | 1 | 32 | 1 |  |
| 542F | I/O #47 | Baud rate | 0 | 4 | 0 |  |
| 5430 | I/O #48 | Lost command | 0 | 2 | 0 |  |
| 5431 | I/O #49 | Time out | 1 | 1200 | 1 | 0.1sec |
| 5432 | I/O #50 | Auto mode | 0 | 2 |  |  |

< EXT Group >

| Address | No. | Description | Default | Max. value | Min.value | Unit |
| --- | --- | --- | --- | --- | --- | --- |
| 5501 | EXT #01 | Sub B/D | 0 | 8 | 0 |  |
| 5532 | EXT #50 | OPT B/D | 0 | 3 | 0 |  |
| 5533 | EXT #51 | OPT mode | 0 | 3 | 0 |  |
| 555A | EXT #90 | Station ID | 1 | 63 | 0 |  |