Data Sheet

LG Programmable Logic Controller

FieldBus Network Single Remote module

G0L-SMQA

G0L-SMIA

G0L-SMHA

GLOFA-GM

LG Industrial Systems

● Beijing Branch             	● Bangkok Branch

LG Industrial Systems 		LG Industrial Systems (Thailand)

Elevator Co., Ltd. 		Co., Ltd

T : +86-10-6462-3256                  T : +66-2-381-8443

F : +86-10-6462-3255                  F : +66-2-381-8445

● Bogota Branch          	● Chicago Branch

LG Industrial Systems de 	LG Industrial Systems Co., Ltd.

Colombia S.A.    		Chicago Office

T : +57-1-310-6077                   T : +1-708-692-4500

F : +57-1-310-5831                   F : +1-708-692-4501

● Dalian Branch              	● Hanoi Branch

Dalian LG Industrial Systems 	LG Industrial Systems Co., Ltd.

Co., Ltd.      		Hanoi Office

T : +86-411-281-2579                  T : +64-4-821-0388

F : +86-411-281-2578                  F : +64-4-821-0399

● Hong Kong Branch         	● Shanghai Branch

LG Industrial Systems (HK) Ltd.   Shanghai LG Industrial Systems Co., Ltd.

T : +852-2598-6615                    T : +86-21-6248-2710

F : +852-2598-7105                    F : +86-216248-3236

● Singapore Branch          	● Taipei Branch

LG Industrial Systems Co., Ltd.    LG Industrial Systems (Taiwan) Co. Ltd.

T : +65-323-7361                      T : +886-2-516-5010

F : +65-323-7362                      F : +886-2-516-5035

● Tokyo Branch

LG Industrial Systems Co., Ltd. Tokyo Office

T : +81-3-3589-6362

F : +81-3-3588-1810

LG Industrial Systems Co., Ltd.

● Head Office

LG Mullae Building 9th F, 10, Mullae-dong 6-ga, Yongdungpo-gu, Seoul, KOREA

Tel : +82-2-2006-3751~6     Fax : +82-2-2006-3951

Home page : http:www.lgis.lg.co.kr/fa

702005638

Before handling the product

Read this data sheet carefully prior to any operation, mounting, installation or start-up of the product.

Materials for GLOFA GM

| Name | Code |
| --- | --- |
| GLOFA GMWIN (Programming software) | 702005047 |
| GLOFA GMWIN (Instruction & Programming) | 702005058 |
| GLOFA GM3/4 (User’s Manual) | 702005581 |
| GLOFA GM6 (User’s manual) | 702005581 |
| GLOFA GM Fnet/Mnet (User’s manual) | 702005070 |

| Name | GLOFA-GM Fnet single remote Data Sheet |
| --- | --- |
| Code | 702005638 |

 Safety Precautions

Be sure to read carefully the safety precautions given in data sheet and user’s manual before operating the module and follow them.

The precautions explained here only apply to the GLOFA Fnet single remote modules.

For safety precautions on the PLC system, please see the GLOFA GM Fnet user’s manual.

If not provided with proper prevention, it can cause death, fatal injury or considerable loss or property

If not properly observed, it can cause a hazard situation to result in severe or slight injury or a loss of property.

WARNING

!

CAUTION

!

A precaution is given with a hazard alert triangular symbol to call your attention, and precautions are represented as follows according to the degree of hazard.

However, a precaution followed with    CAUTION  can also result in serious condition. Both of two symbols indicate that an important content is mentioned, therefore, be sure to observe it.

Keep this manual handy for your quick reference in necessary.

 Design Precaution

CAUTION

Do not run I/O signal lines near to high voltage line or power line. Separate them as 100mm or more as possible. Otherwise, noise can cause module malfunction

 Installation Precaution

CAUTION

Operate the PLC in the environment conditions given in the general specifications

If the PLC is operated in other environment not specified in the general specification, it can cause an electric shock, a fire, malfunction or damage or degradation of the module.

Make sure the module fixing projections is inserted into the module fixing hole and fixed.

Improper installation of the module can cause malfunction, disorder or falling.

 Wiring Precautions

CAUTION

CAUTION

When grounding a FG terminal, be sure to provide class 3 grounding which is dedicated to the PLC.

Before the PLC wiring, be sure to check the rated voltage and terminal arrangement for the module and observe them correctly.

Drive the terminal screws firmly to the defined torque. If loosely driven, it can cause short circuit, fire or malfunction.

Be careful that any foreign matter like wire scraps should not enter into the module. It can cause a fire, disorder or malfunction.

 Test RUN and Maintenance Precautions

WARNING

Do not contact the terminals while the power is applied. It can cause malfunction.

When cleaning or driving terminal screws, perform them after the power has been turned off.

Do not perform works while the power is applied. It can cause disorder or malfunction.

Do not separate the PCB from the case of module, or do not remodel the module. They can cause disorder, malfunction, damage of the module or a fire.

 Waste Disposal Precautions

CAUTION

When disposing the module, do it as an industrial waste.

1. Introduction

This data sheet contains the brief information about the characteristics, configurations, and operating of GLOFA PLC Fnet single remote modules.

2. General Specifications

| No. | ###### Item | Specification |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55℃ |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70℃ |  |  |  |  |  |  |
| 3 | Operating Humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  | IEC 1131-2 |
|  |  | Frequency | Acceleration |  | Amplitude |  | Sweep count | IEC 1131-2 |
|  |  | 10≤f∠57 Hz | - |  | 0.075 mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57 ≤f≤150 Hz | 9.8㎨ {1G} |  | - |  |  |  |
|  |  | Continuos vibration |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  | Amplitude |  |  |  |
|  |  | 10≤f∠57 Hz | - |  | 0.035 mm |  |  |  |
|  |  | 57≤f≤150 Hz | 4.9㎨{0.5G} |  | - |  |  |  |
| 6 | Shocks | *Maximum shock acceleration: 147㎨ {15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  | IEC 1131-2 |
| 7 | Noise immunity | Square wave impulse noise | ±1,500 V |  |  |  |  |  |
|  |  | Electrostatic discharge | Voltage :4kV(contact discharge) |  |  |  |  | IEC 1131-2 IEC 801-2 |
|  |  | Radiated electromagnetic field | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC 1131-2 IEC 801-3 |
|  |  | Fast transient burst noise | Severity Level | All power modules | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os |  | IEC 1131-2 IEC 801-4 |
|  |  |  | Voltage | 2 kV | 1 kV | 0.25 kV |  |  |
| 8 | Atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |

3. Performance Specifications

| Model Item | G0L-SMQA | G0L-SMIA | G0L- SMHA |
| --- | --- | --- | --- |
| Transfer rate | 1Mbps |  |  |
| Dropout tolerance | 20ms |  |  |
| Comm. Method | Half duplex bit serial method |  |  |
| Synchronization | Frame synchronous method |  |  |
| Transmission method | Bus type |  |  |
| Max. cable length | 750m |  |  |
| Numbers of station | Up to 64 stations |  |  |
| Modulation | Manchester Biphase-L |  |  |
| Error detect | CRC-CCITT and Time Over |  |  |
| Connector type | 9 pin plug type |  |  |
| Cable type | Twisted pair cable |  |  |
| Max. link points | 3,840 Word |  |  |
| Max. transfer points | 1,920 Word |  |  |
| Power Supply | DC24V |  |  |
| Current Consumption | 284mA | 111mA | 272mA |
| Weight | 406g | 350g | 378g |

4. Cable Specifications

 Twisted pair cable

| Type | LIREV-AMESB 2*1.0mm 18AWG | Structure |
| --- | --- | --- |
| Manufacturer | LG Cable | Conductor Insulator Shield Ground line |
| Cable Type | Twisted pair shielded cable |  |
| Impedance | 21.8Ω/㎞ |  |
| Withstanding Voltage(DC) | 500 V/Min |  |
| Insulation resistance | 1,000㏁/㎞ or more |  |
| Capacity | 45 ㎊/m or less (1㏀) |  |
| Characteristic impedance | 120±12Ω(10㎒) |  |
| No. of core | 2 Core |  |

5. Wiring of Communication Cable

Cable for electric network connection uses only No. 6 and No. 7 of the connector pins. No.6 and No. 7 should be connected with the pin has the same pin number. Each body of connector should be connected with shield wire.

6

7

6

7

6

7

6

7

Shield wire

6. Terminal Resistor

pin 7

pin

6

resistor

 Resistor : 110, 1/2W

 Connection : Pin 6 and 7

① Attach 110, 1/2W resistor of spare parts to the connectors of both end of network

② Connector case should not be contacted with terminal resistor.

9-pin socket type

7. Parts Name and Descriptions

| G0L-SMQA Connector (CON1, 2) |  | Connectors for FieldBus communication cable (Electrical) |
| --- | --- | --- |
| Master station No. setting switch |  | 00 ~ 63 (Decimal) |
| ×10 |  | Set ten’s figure of station number |
| ×1 |  | Set one’s figure of station number |
| LED |  | Indicates the status of communication |
| PWR |  | Turn on when power is applied |
| TRX |  | Flickering while normal communication |
| ERR |  | Turn on when an error occurs |
| Mode switch |  | Emergency data output setting |
| 1 | Off | Latches the last data during communication error |
|  | On | Outputs user-defined data during communication error |
| 2 |  | Not used |
| LED |  | Indicates input/output data |

x 10

x 1

PWR

ERR

x10

MODE

On

M-STATION NO.

S-STATION NO.

x1

TRX

Off

G0L-SMQA

FG    0     1      2     3

COM1  4       5     6     7   COM2

24V

INPUT

DC 24V

8      9    10    11

COM3   12    13    14     15

COM4

24G

| Local Station No. setting switch | 00 ~ 63 (Decimal) |
| --- | --- |
| ×10 | Set ten’s figure of station number |
| ×1 | Set one’s figure of station number |
| Terminal Block | Connect external power supply (See 7.2 for more details) |
| 0 ~ 15 | Input / Output terminals |
| COM1 ~ COM4 | Common terminals |
| FG | Frame ground terminal |
| 24V | +24VDC |
| 24G | -24VDC |

8. Installation

- Install the option module while the power of PLC system is off.

- All communication modules of whole network system should have different station number. Duplicated station number will cause serious communication error.

- Use the cable as recommended specification. Otherwise, it can cause communication error.

- Install terminal resistor which are contained as spare parts at the CON1 or CON2 terminal of the last module of network

- Place communication cable away from power cable or inductive noise source as much as possible.

- If the power of master station is reset during communication, the remote station will resume the operation according to the initialization program of the master station. Therefore, be sure to make initialization program at the master station.

9. Maintenance

To keep the module as the best condition, perform the daily and regular check as followings.

- Daily Check

| Items to be checked |  | Contents | Criteria of decision | Action to take |
| --- | --- | --- | --- | --- |
| Cable connection status |  | Release of cable | Shall not be any release | Tighten the cable |
| Module connection status |  | Release of screw | Shall not be any release | Tighten the screw |
| LED Indication | PWR | LED status | LED is on (Off means an error) | Check the power cable |
|  | TRX |  | LED is on. (Off means duplicated station or wrong cable connection) | Check the cable, station number, or communication frame |
|  | ERR |  | LED is off. Regular flickering : system error Irregular flickering : communication frame error |  |

- Regular Check

| Check item |  | How to check | Criteria of decision | Action to take |
| --- | --- | --- | --- | --- |
| Ambient conditions | Ambient temp. | Measure thermometer/hygrometer | 0-55℃ | Adjust it in order to fit to the general specifications. (for use in panel, inside panel ambient criteria) |
|  | Ambient moisture |  | 5-95% RH |  |
|  | Ambient pollution | Measure corrosive gas | Corrosive gas shall not be there. |  |
| Module state | Loosening, Shaking | Move communication module | It shall be tightly mount-ed. | Tighten screw |
|  | Dust, Foreign matters | Visual inspection | No dust or foreign matters shall be there. |  |
| Connection state | Terminal screw loosened | Tighten with driver | No loosening shall be there. | Tighten |
|  | Closeness of compressed terminal | Visual inspection | Distance shall be suit-able. | Correct |
|  | Connector loosening | Visual inspection | No loosening shall be there. | Tighten connector lock-ing screw. |
| Power voltage check |  | Measure voltage between DC24V +/- terminals | DC 20 ~ 30V | Modify power supply. Modify transformer tap. |

10. Troubleshooting

Error occurs

Check the proper voltage is applied to the module.

Is the PWR LED off?

YES

A

A

NO

Reapply the power to the module.

Is the TRX LED is on?

YES

NO

NO

Does it operate properly?

YES

END

This is the hardware error of communication module. Contact the nearest service station.

This is the hardware error of communication module. Contact the nearest service station.

YES

Check and repair the network cable.

NO

Place the network cable away from power cable or inductive noise source as much as possible.

Are network cables open or short?

Is the network

cable placed near to power cables or inductive noise source?

A

YES

NO

Use repeater or reduce the cable length within specified range.

Change the station number so as not to be duplicated

Network check

Are there

duplicated station numbers in

entire network?

Does cable length exceed specified range?

Is terminal

resistor connected at both ends of network?

NO

Connect terminal resistance at both ends of network.

YES

Check and repair the network cable.

Are network cables open or short?

YES

NO

Check the entire network so as not to be a closed circuit.

Is the entire network a closed circuit?

YES

This is the hardware error of communication module. Contact the nearest service station.

NO

NO

YES

YES

NO

END

I/O error check

Are there

duplicated station numbers in

entire network?

Change the station number so as not to be duplicated

YES

NO

Check the connection status of network cable.

Is the network cable connected properly?

YES

NO

Is terminal

resistor connected at both ends of network?

Connect terminal resistance at both ends of network.

NO

YES

NO

Place the network cable away from power cable or inductive noise source as much as possible.

Is the network

cable placed near to power cables or inductive noise source?

YES

This is the hardware error of communication module. Contact the nearest service station.

END

11. Dimensions

The dimensions of G0L-SMIA, G0L-SMQA, and G0L-SMHA are same.

(Unit : mm)

Ø4

142

150

On

Off

24V

24G

x 10

x 1

PWR

ERR

MODE

M-STATION NO.

S-STATION NO.

x10

x1

TRX

100

88.5

INPUT

DC 24V

35

44.3