# Specifications

## General specifications

| No. | Item | Specification |  |  |  |  |  |  | Standard |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Operating temperature | 0 ~ 55 ℃ |  |  |  |  |  |  |  |
| 2 | Storage temperature | -25 ~ 70 ℃ |  |  |  |  |  |  |  |
| 3 | Operating humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |  |
| 4 | Storage humidity | 5 ~ 95%RH, non-condensing |  |  |  |  |  |  |  |
| 5 | Vibration | Occasional vibration |  |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  |  | Amplitude |  | Sweep count | IEC61131-2 |
|  |  | 10  f  57Hz |  |  |  | 0.075mm |  | 10 times in each direction for X, Y, Z |  |
|  |  | 57  f  150Hz | 9.8m/s2{1G} |  |  |  |  |  |  |
|  |  | Continuous vibration |  |  |  |  |  |  |  |
|  |  | Frequency | Acceleration |  |  | Amplitude |  |  |  |
|  |  | 10  f  57Hz |  |  |  | 0.035mm |  |  |  |
|  |  | 57  f  150Hz | 4.9m/s2{0.5G} |  |  |  |  |  |  |
| 6 | Shocks |  Maximum shock acceleration:: 147 m/s2{15G} *Duration time :11 ms *Pulse wave: half sine wave pulse( 3 times in each of X, Y and Z directions ) |  |  |  |  |  |  | IEC61131-2 |
| 7 | Noise immunity | impulse noise |  |  1,500 V |  |  |  |  | LGIS Standard |
|  |  | Electrostatic discharge |  | Voltage :4kV(contact discharge) |  |  |  |  | IEC61131-2 IEC1000-4-2 |
|  |  | Radiated electromagnetic field |  | 27 ~ 500 MHz, 10 V/m |  |  |  |  | IEC61131-2, IEC1000-4-3 |
|  |  | Fast transient burst noise |  | Severity Level | All power modules |  | Digital I/Os ( Ue  24 V) | Digital I/Os (Ue  24 V) Analog I/Os communication I/Os | IEC61131-2 IEC1000-4-4 |
|  |  |  |  | Voltage | 2kV |  | 1kV | 0.25kV |  |
| 8 | Operating atmosphere | Free from corrosive gases and excessive dust |  |  |  |  |  |  |  |
| 9 | Altitude for use | Up to 2,000m(6,562ft) |  |  |  |  |  |  |  |
| 10 | Pollution degree | 2 or lower |  |  |  |  |  |  |  |
| 11 | Cooling method | Self-cooling |  |  |  |  |  |  |  |

1) IEC(International Electrotechnical Commission)

: The international civilian organization which produces standards for electrical and electronics industry.

2) Pollution degree

: It indicates a standard of operating ambient pollution level.

The pollution degree 2 means the condition in which normally, only non-conductive pollution occurs.  Occasionally, however, a temporary conductivity caused by condensation shall be expected.

Remark

## Performance Specifications

### Performance specifications

| Item |  | Specifications |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | G4F-HO1A | G6F-HO1A | G4F-HD1A | G6F-HD1A |
| Occupied I/O points |  | 64 points |  |  |  |
| Number of channels |  | 2 |  |  |  |
| Count input signal | Phase | Phase A, Phase B |  |  |  |
|  | Level | DC5/12/24V |  | EIA RS-422A standard |  |
|  | Type | Open Collector |  | Line Driver |  |
| Counting range |  | -2,147,483,648 ~ 2,147,483,647 (binary 32 bits) |  |  |  |
| Counting speed |  | 200 KHz (Max) |  | 500 KHz(Max) |  |
| Up/Doun count setting | 1 Phase input | Program or Phase B |  |  |  |
|  | 2 Phase input | Difference of phases |  |  |  |
|  | CW/CCW | Phase A input : Up count |  |  |  |
|  |  | Phase B input : Down count |  |  |  |
| External output | Coincidence output | Out 0 Out 1 Out 2 Out 3 (>, =, < ,≤≤, ≥≤) Transistor output (Open collector, 10 ~ 30V) |  |  |  |
| External input | Preset | DC 5V / 12V / 24V |  |  |  |
|  | Gate | DC 5V / 12V / 24V |  |  |  |
| Multiplication | 1 Phase input | 1, 2 multiple of phase (set by program) |  |  |  |
|  | 2 Phase input | 1, 2, 4 multiple of phase (set by program) |  |  |  |
| Functions |  | Count Clear, Count Latch, Sampling Count, Pulse frequency count, Periodic pulse count |  |  |  |
| Internal current consumption |  | 400㎃ | 450㎃ | 400㎃ | 450㎃ |
| Weight |  | 173 g | 126g | 184 g | 134 g |

### Input specifications

| Item | Level | Specifications |  |
| --- | --- | --- | --- |
|  |  | Open collector type | Differential input type |
| On-state voltage(Min) | DC 5 V | 4.5 V | EIA RS-422A standard |
|  | DC 12 V | 11 V |  |
|  | DC 24 V | 14 V |  |
| Off-state voltage(Max) | DC 5 V | 0.8 V |  |
|  | DC 12 V | 1.5 V |  |
|  | DC 24 V | 2.5 V |  |

### Preset, Gate Input / Transistor output specifications

| Item | Level |  |
| --- | --- | --- |
| Input voltage | DC 5V / 12V / 24V |  |
| On-state voltage(Min) | DC 5V | DC 4.5V |
|  | DC 12V | DC 11V |
|  | DC 24V | DC 14V |
| Off-state voltage(Max) | DC 5V | DC 0.8V |
|  | DC 12V | DC 1.5V |
|  | DC 24V | DC 2.5V |
| On Delay Time | 1ms or less |  |
| Off Delay Time | 1ms or less |  |
| Coincidence output | DC 24V, 100 mA/point |  |
| Leakage current | 0.1 mA or less |  |
| Voltage drop | 2.5 V or less |  |
| On Delay Time | 0.1 ms or less |  |
| Off Delay Time | 0.1 ms or less |  |

## Part Identification Nomenclature

### Part identification

| 1) G4F-HO1A | 2) G4F-HD1A | 3) G6F-HO1A | 4) G6F-HD1A |
| --- | --- | --- | --- |
| ① ② | ① ② | ① ② | ① ② |

| No | Name |  | Description |
| --- | --- | --- | --- |
| ① | LED | A | Phase A |
|  |  | B | Phase B |
|  |  | P | External Preset |
|  |  | G | External Gate |
|  |  | OUT0 | OUT0 Coincidence output |
|  |  | OUT1 | OUT1 Coincidence output |
|  |  | OUT2 | OUT2 Coincidence output |
|  |  | OUT3 | OUT3 Coincidence output |
|  |  | READY | Ready |
| ② | Connector |  | Terminal for connecting with external device |

### Input/Output terminal

#### Pin arrangement

##### G4F-HO1A/ G6F-HO1A

| Terminal | Pin Number |  | Description |  |
| --- | --- | --- | --- | --- |
|  | CH0 | CH1 |  |  |
|  | 1 | 15 | A12V | Phase A DC12V |
|  | 2 | 16 | A24V | Phase A DC24V |
|  | 3 | 17 | AB_C | Phase A/B Common |
|  | 4 | 18 | A5V | Phase A DC5V |
|  | 5 | 19 | B12V | Phase B DC12V |
|  | 6 | 20 | B24V | Phase B DC24V |
|  | 7 | 21 | P24V | Preset DC24V |
|  | 8 | 22 | B5V | Phase B DC5V |
|  | 9 | 23 | P5V | Preset DC5V |
|  | 10 | 24 | P12V | Preset DC12V |
|  | 11 | 25 | G24V | Gate DC24V |
|  | 12 | 26 | PG_C | Preset/Gate Common |
|  | 13 | 27 | G5V | Gate DC5V |
|  | 14 | 28 | G12V | Gate DC12V |
|  | 29 | 33 | OUT1 | OUT1 Coincidence output |
|  | 30 | 34 | OUT0 | OUT0 Coincidence output |
|  | 31 | 35 | OUT3 | OUT3 Coincidence output |
|  | 32 | 36 | OUT2 | OUT2 Coincidence output |
|  | 37 | 38 | 24V | DC24V External source |
|  | 39 | 40 | 24G |  |

##### G4F-HD1A/ G6F-HD1A

| Terminal | Pin Number |  | Description |  |
| --- | --- | --- | --- | --- |
|  | CH0 | CH1 |  |  |
|  | 1 | 15 | A- | A- 입력 |
|  | 2 | 16 | A+ | A+ 입력 |
|  | 3 | 17 | - | - |
|  | 4 | 18 | - | - |
|  | 5 | 19 | B- | B- 입력 |
|  | 6 | 20 | B+ | B+ 입력 |
|  | 7 | 21 | P24V | Preset DC24V |
|  | 8 | 22 | - | - |
|  | 9 | 23 | P5V | Preset DC5V |
|  | 10 | 24 | P12V | Preset DC12V |
|  | 11 | 25 | G24V | Gate DC24V |
|  | 12 | 26 | PG_C | Preset/Gate Common |
|  | 13 | 27 | G5V | Gate DC5V |
|  | 14 | 28 | G12V | Gate DC12V |
|  | 29 | 33 | OUT1 | OUT1 Coincidence output |
|  | 30 | 34 | OUT0 | OUT0 Coincidence output |
|  | 31 | 35 | OUT3 | OUT3 Coincidence output |
|  | 32 | 36 | OUT2 | OUT2 Coincidence output |
|  | 37 | 38 | 24V | DC24V External source |
|  | 39 | 40 | 24G |  |

#### Internal Circuit

##### G4F-HD1A/ G6F-HD1A

| I/O classification | Internal circuit | No. | Terminal (CH0,CH1) | Description |  | Description |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Ch0 | Ch1 |  |
| Input | ③ ① ② ④ | ① | A24V | 2 | 16 | Phase A input(DC24V) |
|  |  | ② | A12V | 1 | 15 | Phase A input(DC12V) |
|  |  | ③ | A5V | 4 | 18 | Phase A input(DC5V) |
|  |  | ④ | AB_COM | 3 | 17 | Phase A,B common |
|  |  | ① | B24V | 6 | 20 | Phase B input(DC24V) |
|  |  | ② | B12V | 5 | 19 | Phase B input(DC12V) |
|  |  | ③ | B5V | 8 | 22 | Phase B input(DC5V) |
|  | ⑦ ⑤ ⑥ ⑧ | ⑤ | P24V | 7 | 21 | Preset (DC 24V) |
|  |  | ⑥ | P12V | 10 | 24 | Preset (DC 12V) |
|  |  | ⑦ | P5V | 9 | 23 | Preset (DC 5V) |
|  |  | ⑧ | PG_COM | 12 | 26 | Preset, Gate common |
|  |  | ⑤ | G24V | 11 | 25 | Gate (DC 24V) |
|  |  | ⑥ | G12V | 14 | 28 | Gate (DC 12V) |
|  |  | ⑦ | G5V | 13 | 27 | Gate (DC 5V) |
| Output | ⑭ ⑨ ⑩ ⑪ ⑫ ⑬ | ⑨ | OUT0 | 30 | 34 | Coincidence output 0 |
|  |  | ⑩ | OUT1 | 29 | 33 | Coincidence output 1 |
|  |  | ⑪ | OUT2 | 32 | 36 | Coincidence output 2 |
|  |  | ⑫ | OUT3 | 31 | 35 | Coincidence output 3 |
|  |  | ⑬ | 24V | 37 | 38 | External source DC 24V |
|  |  | ⑭ | 24G | 39 | 40 | External source COM |

##### G4F-HD1A/ G6F-HD1A

| I/O classification | Internal circuit | No. | Terminal (CH0,CH1) | Description |  | Description |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Ch0 | Ch1 |  |
| Input | ① ② ③ ④ | ① | A+ | 2 | 16 | Phase A+ input |
|  |  | ② | A- | 1 | 15 | Phase A- input |
|  |  | ③ | B+ | 6 | 20 | Phase B+ input |
|  |  | ④ | B- | 5 | 19 | Phase B- input |
|  | ⑦ ⑤ ⑥ ⑧ | ⑤ | P24V | 7 | 21 | Preset (DC 24V) |
|  |  | ⑥ | P12V | 10 | 24 | Preset (DC 12V) |
|  |  | ⑦ | P5V | 9 | 23 | Preset (DC 5V) |
|  |  | ⑧ | PG_COM | 12 | 26 | Preset, Gate common |
|  |  | ⑤ | G24V | 11 | 25 | Gate (DC 24V) |
|  |  | ⑥ | G12V | 14 | 28 | Gate (DC 12V) |
|  |  | ⑦ | G5V | 13 | 27 | Gate (DC 5V) |
| Output | ⑭ ⑨ ⑩ ⑪ ⑫ ⑬ | ⑨ | OUT0 | 30 | 34 | Coincidence output 0 |
|  |  | ⑩ | OUT1 | 29 | 33 | Coincidence output 1 |
|  |  | ⑪ | OUT2 | 32 | 36 | Coincidence output 2 |
|  |  | ⑫ | OUT3 | 31 | 35 | Coincidence output 3 |
|  |  | ⑬ | 24V | 37 | 38 | External source DC 24V |
|  |  | ⑭ | 24G | 39 | 40 | External source COM |

## Basic usage

■ The High-speed count module can count high-speed pulse which cannot be proceed with the CPU counting instructions (CTU,CTUD, etc.). Up to 32 bits binary (-2,147,483,648 ~ 2,147,483,647) can be counted.

■ High speed count module has 7 pulse input modes; 1 phase multiple of 1(up/down count by program), 1 phase multiple of 2(up/down count by program), 1 phase multiple of 1(up/down count by phase B), 1 phase multiple of 2(up/down count phase B),CW/CCW, 2 phase multiple of 1, 2 phase multiple of 2, 2 phase multiple of 4.

■ High speed count module has 2 up/down counting method ;

1 phase : set by program, set by phase B

2 phase : set by difference of phases

CW/CCW : phase A input = increment,  Phase B input = decrement

■ High speed count module has 5 functions ;

Count clear, Count latch, Sampling count, Pulse frequency count, and Periodic pulse count.

### Pulse input modes

#### 1 Phase pulse input

##### Up/down count by program

(A) 1 phase multiple of 1

Counting is executed at the rising edge of phase A and either up count or down count is selected by program.

| Low/high | Phase A rise | Phase A fall |
| --- | --- | --- |
| Up/down count selecting signal Off | Up count | - |
| Up/down count selecting signal On | Down count | - |

Phase A

Up

Down

Up

Up/down count selecting signal

Count

10

11

12

13

12

11

10

11

(B) 1 phase multiple of 2

Counting is executed at the rising edge/ falling edge of phase A and either up count or down count is selected by program.

| Low/high | Phase A rise | Phase A fall |
| --- | --- | --- |
| Up/down count selecting signal Off | Up count | Up count |
| Up/down count selecting signal On | Down count | Down count |

Phase A

Up/down count selecting signal

Up

Count

Up

Down

11

10

12

13

14

15

16

15

14

13

12

11

10

11

12

##### Up/down count by phase B

(A) 1 phase multiple of 1

Counting is executed at the rising edge of phase A and either up count or down count is selected by phase B.

| Low/high | Phase A rise | Phase A fall |
| --- | --- | --- |
| Phase B Low | Up count | - |
| Phase B High | Down count | - |

Up

Down

Up

Phase B

Count

Phase A

10

9

8

7

8

9

10

9

(B) 1 phase multiple of 2

Counting is executed at the rising edge/ falling edge of phase A and either up count or down count is selected by phase B.

| Low/high | Phase A rise | Phase A fall |
| --- | --- | --- |
| Phase B Low | Up count | Up count |
| Phase B High | Down count | Down count |

Up

Up

Down

Phase B

Count

Phase A

10

10

9

8

7

6

5

4

5

6

7

8

9

11

12

#### 2 phase (up/down count by difference of phases)

##### 2 phase multiple of 1

Up/down count is executed by the difference of phase A and phase B.

When phase A leads phase B,Up count is executed at the rising edge of phase A, when phase B leads phase B down count is executed at the falling edge of pahse A.

Phase B

Count

Phase A

Up

Down

10

11

12

13

12

11

10

9

##### 2 phase multiple of 2

Up/down count is executed by the difference of phase A and phase B at the rising edge and falling edge of phase A.

when phase A leads phase B up count is executed and when phase B leads phase A  down count is executed.

Phase B

Phase A

Up

Down

Count

10

11

12

13

14

15

12

11

15

16

17

16

14

13

10

##### 2 phase multiple of 4

Up/down count is executed by the difference of phase A and phase B at the rising edge and falling edge of phase A / pahse B.

when phase A leads phase B up count is executed and when phase B leads phase A  down count is executed.

Phase A

Up

Down

Count

10

Phase B

11

12

13

14

15

16

17

18

19

20

21

22

23

22

21

20

19

18

17

16

15

14

13

12

11

12

#### CW(Clockwise)/CCW(Counter Clockwise)

Counting is executed at the rising edge/ falling edge of phase A and phase B.

The relationship between phase A pulse input and phase B pulse input is shown below.

Phase B

Count

Phase A

Up

Down

7

8

9

10

11

9

8

10

7

### Count mode

■ Count is used 2 method as follows according to function.

| Selection | GLOFA GM | MASTER-K |
| --- | --- | --- |
|  | Function block HSCB_MOD’s SEL | Address 1 for Ch 0, 33 for Ch1 |
| Linear count | “0” | “0” |
| Ring count | “1” | “1” |

#### Linear count

■ Count range : -2,147,483,648 ~ 2,147,483,647 ( 32bit signed binary values)

■ When count value reaches at the maximum value carry is occurs and when count value reaches at the minimum value borrow is occurred.

■ If carry occurs, counting stops and no more up-count is performed but down-count is possible.

■ If borrow occurs, counting stops and no more down-count is performed but up-count is possible.

+2,147,483,647

Down

Up

Borrow

Carry

-2,147,483,648

#### Ring count

■ Count range : user-defined minimum value ~ user-defined maximum value.

■ Count display: when performing the ring count, the user-defined minimum value is displayed but maximum value is not displayed. This is same at up count and down count.

##### Up count

■ when the count value exceeds the user-defined maximum value, carry occurs but the counting is executed continuously. Detail figure for up count is shown as below.

Carry

User-defined maximum value

Preset value

User-defined minimum value

○:Not including

●:Including

##### Down count

■ when the count value exceeds the user-defined minimum value, borrow occurs but the counting is executed continuously. Detail figure for up count is shown as below.

Barrow

User-defined maximum value

Preset value

User-defined minimum value

○: Not including

●: Including

##### Ring count execution according to the preset value (for up count)

■ When the preset value is set out of the user-defined maximum / minimum value.,

- Count value increases and at the user-defined minimum value if adding one pulse, the count value goes up to the user-defined maximum value and then up count goes on.

- When the count value exceeds 2,147,483,647, carry occurs and the count value goes down to

–2,147,483,648 and then up count goes on.

■ When the preset value is set within the user-defined maximum / minimum value.,

- Up count value increases and at the user-defined maximum value if adding one pulse, the count value goes down to the user-defined minimum value and then up count goes on.

- When the count value goes from the user-defined maximum value to user-defined minimum value, carry occurs.

Carry

Carry

-2,147,483,648

2,147,483,647

User-defined maximum value

User-defined minimum value

※Within user-defined value

※Out of user-defined value

○: Not including

●: Including

##### Ring count execution according to preset value (for down count)

■ When the preset value is set out of the user-defined maximum / minimum value.,

- Count value decreases and at the user-defined maximum value if adding one pulse, the count value goes up to the user-defined minimum value and then down count goes on.

- When the count value exceeds -2,147,483,647, borrow occurs and the count value goes down to 2,147,483,648 and then down count goes on.

■ When the preset value is set within the user-defined maximum / minimum value.,

- Down count value exceeds and at the user-defined minimum value if adding one pulse, the count value goes up to the user-defined maximum value and then down count goes on.

- When the count value goes from user-defined minimum value to the user-defined maximum value, borrow occurs.

2,147,483,647

User-defined maximum value

-2,147,483,648

User-defined minimum value

※Within user-the defined value

Borrow

Borrow

○:Not including

●: Including

※ out of the user-defined value

Remark

1.Whether the ring count value is counted within the user defined value or not, it depends on the count value

at the time when the ring count is set.

2.When using the ring count, be sure to set the count value within the user defined value by using the preset

value.

### Coincidence output

■ Coincidence output is a function which compares current count value with the user-defined value and output when the condition matches.

■ Coincidence output can be set for 4 outputs in each channel and used independently.

■ Coincidence output conditions can be set in 7 methods by >, = , <,  combination.

| Conditions | GLOFA GM | MASTER-K |
| --- | --- | --- |
|  | Function block HSCB_CMP’s CMPS | Output; Ch 0; Ch1 1. Out0; Address 3; Address 35. Out1; Address 4; Address 36. Out2; Address 5; Address 37. Out3; Address 6; Address 38. |
| Count value < User-defined value | “0” | “0” |
| Count value≤User-defined value | “1” | “1” |
| Count value = User-defined value | “2” | “2” |
| Count value≥User-defined value | “3” | “3” |
| Count value > User-defined value | “4” | “4” |
| User-defined value1 ≤ Count value ≤ User-defined value2 | “5” | “5” |
| User-defined value1≥ Count value, Count value ≥ User-defined value2 | “6” | “6” |

■ To use coincidence output, turn on the coincidence output enable command and the comparing enable command.

| Signals | GLOFA GM | MASTER-K |
| --- | --- | --- |
| Comparing enable command (LED Output) | Function block HSCB_OUT CMP_E = 1 | Ch 0 P (n+2) 4, Ch1 P (n+3) 4 “On” |
| Output enable command (External output) | Function block HSCB_OUT OUT_E = 1 | Chj0 P (n+2) 5, Ch1 P (n+3) 5 “On” |
| Coincidence output signal | Function block HSCB_OUT EQ0_R~EQ3_R = 1 (Independently) | Ch0 P(n+2)6~P(n+2)9 , Ch1 P(n+3)6~P(n+3)9 “On” (Independently) |

■ If the coincidence output enable command is turned on and the comparing enable command is off, only LED is lit and the coincidence output is turned on.

#### Coincidence output mode 0  (count value < user-defined value)

■ The coincidence output is turned on when the count value is fewer than the user-defined value.

If the count value equals to or more than the user-defined value the coincidence output is turned off.

123456

123457

123458

123459

123460

123461

123462

123460

Count

user-defined value

Comparing enable command

LED

Coincidence output

Coincidence output enable command

#### Coincidence output mode 1(count value ≤ user-defined value)

■ The coincidence output is turned on when the count value is equal to or less than the user-defined value.

If the count value is more than the user-defined value the coincidence output is turned off.

123456

123457

123458

123459

123460

123461

123462

123460

Count

user-defined value

Comparing enable command

LED

Coincidence output

Coincidence output enable command

#### Coincidence output mode 2(count value ≤ user-defined value)

■ The coincidence output is turned on when the count value is equal to the user-defined value.

If the coincidence output is ON, though the count value is not equal to the user-defined value, the coincidence output is not turned off.

To turn off the coincidence output, the coincidence output reset command should be ON.

Coincidence output enable command

123456

123457

123458

123459

123460

123461

123462

123457

Count

User-defined value

Comparing enable command

LED

Coincidence output

123460

Coincidence output reset command

`

#### Coincidence output mode 3 (count value ≤ user-defined value)

■ The coincidence output is turned on when the count value is equal to or more than the user-defined value.

If the count value is less than the user-defined value the coincidence output is turned off.

123456

123457

123458

123459

123460

123461

123462

123460

Count

User-defined value

Comparing enable command

LED

Coincidence output

Coincidence output enable command

#### Coincidence output mode 4 (count value ≤ user-defined value)

■ The coincidence output is turned on when the count value is more than the user-defined value.

If the count value is equal to or less than the user-defined value the coincidence output is turned off.

123456

123457

123458

123459

123460

123461

123462

123458

Count

User-defined value

Comparing enable command

LED

Coincidence output

Coincidence output enable command

#### Coincidence output mode 5 (User-defined value1≤ Count value ≤ User-defined value2)

■ The coincidence output is turned on in the case of User-defined value1≤ Count value ≤ User-defined value2. If the count value is not within the section the coincidence output is turned off.

123456

123457

123458

123459

123460

123461

123462

123458

Count

User-defined value1

Comparing enable command

LED

Coincidence output

Coincidence output enable command

User-defined value2

123460

#### Coincidence output mode 6 (Count value≤User-defined value1 or User-defined value2 ≤Count value)

■ The coincidence output is turned on in the case of Count value≤User-defined value1 or User-defined value2 ≤Count value. If the count value is not within the section the coincidence output is turned off.

123456

123457

123458

123459

123460

123461

123462

123458

Count

User-defined value1

Comparing enable command

LED

Coincidence output

Coincidence output enable command

User-defined value22

123461

### Carry

■ Carry occurs

- For linear count, when the count value reaches 2,147,483,647.

- For ring count, when the count value goes from the user-defined maximum value to the user-defined minimum value.

■ State of count when Carry occurs.

- For linear count, if Carry occurs count stops.

- For ring count, though Carry occurs counting goes on.

■ Carry reset

- Carry can be reset by carry/borrow reset command (HSCB_WR Function block’s CY_R).

| Signal | GLOFA GM | MASTER-K |
| --- | --- | --- |
| Carry reset command | Function block HSCB_WR CY_R = 1 | Ch 0 P(n+2)A, Ch 1 P(n+3)A “On” |

### Borrow

■ Borrow occurs

- For linear count, when the count value reaches  -2,147,483,648.

- For ring count, when the count value goes from the user-defined minimum value to the user-defined maximum value.

■ State of count when Borrow occurs.

- For linear count, if Borrow occurs count stops.

- For ring count, though Borrow occurs counting goes on.

■ Borrow reset

- Borrow can be reset by carry/borrow reset command(HSCB_WR Function block’s CY_R).

| Signal | GLOFA GM | MASTER-K |
| --- | --- | --- |
| Borrow reset command | Function block HSCB_WR CY_R = 1 | Ch 0 P(n+2)A, Ch 1 P(n+3)A “On” |

### Supplementary functions

■ High Speed Counter Module has 5 functions. This section describes the functions.

■ For using a supplementary function the function enable command shall be “On”.

| Functions |  | GLOFA GM |  | MASTER-K |  |
| --- | --- | --- | --- | --- | --- |
| Function enable command |  | Function block HSCB_WR AUX_E = 1 |  | Ch 0 P(n+2)3, Ch 1 P(n+3)3 “On” |  |
| F U N C T I O N | Count Clear | Function block HSCB_AUX AUX | - | Ch 0 Address 2, Ch 1 Address 34 | - |
|  | Count Latch |  | Count value display Function block HSCB_CNT LTCH_OLD |  | Count value display Ch 0 Address: 66, 67 Ch 1 Address: 82, 83 |
|  | Sampling count |  | Count value display Function block HSCB_CNT SCNT_NEW |  | Count value display Ch 0 Address: 68, 69 Ch 1 Address: 84, 85 |
|  | Pulse frequency count |  | Count value display Function block HSCB_CNT TIME_A/TIME_B |  | Phase A Ch 0 Address: 70, 71 Ch 1 Address : 86, 87 Phase B Ch 0 Address: 72, 73 Ch 0 Address: 88, 89 |
|  | Periodic count |  | Count value display Function block HSCB_CNT SCNT_NEW, LTCH_OLD |  | Previous count value Ch 0 Address: 66, 67 Ch 1 Address: 82, 83 Current count value Ch 0 Address: 68, 69 Ch 0 Address: 84, 85 |

#### Count Clear

■ In this function, if Function enable command is ON, the count value is turned to 0.

■ How to set

- Selecting function mode 1 -> Function enable command ON .

■ Count clear makes the current count value clear to 0 in each time the function enable command is ON.

Function mode: 1

Function enable command

Count

1000

500

0

500

900

Remark

※Function enable command : When using FB the command is AUX_E and when using the terminal after

setting the supplementary function enable command(AUX_I/E in FB), Use the Gate terminal.

#### Count Latch

■ In this function, if Function enable command is ON, the current count value is latched and stores the value in the internal buffer memory.

■ How to set

- Selecting function mode 2 -> Function enable command ON .

■ Count latch stores the current count value in each time the function enable command is ON.

■ The latched count value is displayed in function block(HSCB_CNT)’s LTCH_OLD.

500

900

Function mode: 2

Function enable command

Latched value

1000

500

0

Count

500

0

1000

0

Remark

※Function enable command : When using FB the command is AUX_E and when using the terminal after

setting the supplementary function enable command(AUX_I/E in FB), Use the Gate terminal.

#### Sampling Count

■ In this function, if Function enable command is ON, Count is executed during the preset sampling time and stores the value in the internal buffer memory.

■ How to set

- Selecting function mode 3 -> Function enable command ON .

■ Sampling count is executed in each time the function enable command is ON.

■ Sampling count value is displayed in function block(HSCB_CNT)’s SCNT_NEW.

■ The signal for displaying The supplementary function run.

- During the preset sampling time, sampling count is executed and at the same time the function run signal(HSCB_RD function block’s AUX_ING) is turned ON.

Function run signal

Preset time

Preset time

Function mode: 3

Function enable command

Sampling count

1000

500

0

Count

500

0

1000

-500

-1000

Remark

※Function enable command : When using FB the command is AUX_E and when using the terminal after

setting the supplementary function enable command(AUX_I/E in FB), Use the Gate terminal.

#### Pulse frequency count

■ In this function, if Function enable command is ON, frequency count of phase A/B is executed every second and stores the value in the internal buffer memory.

■ How to set

- Selecting function mode 4 -> Function enable command ON .

■ During the function enable command is ON, number of the internal clock renewed every second is displayed.

■ By using the renewed internal clock, frequency of each phase can be calculated as follows.

- Frequency = 25,000,000T      ※ T : Number of clock

■ The signal for displaying The supplementary function run.

- During the function enable command is ON, pulse frequency count function is executed and stores the value in the internal buffer memory.

- At the same time, the function run signal is turned ON.

Function run signal

Function mode: 4

Count

500

0

1000

Function enable command

1S

1S

1S

1S

Number of clock

Remark

※Function enable command : When using FB the command is AUX_E and when using the terminal after

setting the supplementary function enable command(AUX_I/E in FB), Use the Gate terminal.

#### Periodic pulse count

■ In this function, if Function enable command is ON, periodic pulse count is executed during the preset time and stores the value in the internal buffer memory.

■ How to set

- Selecting function mode 5 -> Setting the preset time -> Function enable command ON .

■ During the function enable command is ON, number of pulse count is renewed in every the preset time.

■ The renewed pulse count value is displayed on HSCB_CNT function block’s SCNT_NEW and LTCH_OLD.

■ By using the renewed pulse count value, the periodic pulse count value can be calculated as follows.

- Periodic Pulse Count Value = SCNT_NEW – LTCH_OLD

■ If the preset time is 1 minute, reverse per minute(RPM) can be calculated.

- RPM (Reverse Per Minute) = PPUP

※PPU : Number of input pulse,  P : Pulse count per rotation.

■ The signal for displaying The supplementary function run.

- During the function enable command is ON, periodic pulse count function is executed and at the same time, the function run signal is turned ON.

Preset time

Preset time

Function run signal

0

1000

Previous value

(LTCH_OLD)

Preset time

Preset time

설정시간

Preset time

Preset time

Preset time

Preset time

500

Preset time

Preset time

300

Function mode: 5

Count

Function enable command

Current value

(SCNT_NEW)

700

1000

300

700

1000

800

Remark

※Function enable command : When using FB the command is AUX_E and when using the terminal after

setting the supplementary function enable command(AUX_I/E in FB), Use the Gate terminal.