# Installation and Wiring

## Installation

### Installation Ambience

This module has high reliability regardless of its installation ambience. But be sure to check the following conditions for higher reliability and stability of the system.

.

#### Ambience Requirements

Avoid installing this module in places, which are subjected or exposed to:

- Water leakage and dust a large amount of dust, powder and other conductive power, oil mist, salt, of organic solvent.

- Mechanical vibrations of impacts transmitted directly to the module body.

- Direct sunlight.

- Dew condensation due to sudden temperature change.

- High or low temperatures (outside the range of 0-55℃)

#### Installing and Wiring

- During wiring or other work, do not allow any wire scraps to enter into it.

- Install it on locations that are convenient for operation.

- Make sure that it is not located near high voltage equipment on the same panel.

- Make sure that the distance from the walls of duct and external equipment be 50 mm or more.

- Be sure to be grounded to locations that have good noise immunity.

### Handling precautions

1) Do not drop or impact the product.

2) Do not detach PCB from the case, it may cause malfunction.

3) During wiring or other work, do not allow any wire chips get inside the product.

4) Switch the external power off before mounting or removing the module and

the cable.

## Wiring Precautions

When using High-speed inputs, take the following precautions against noise in wiring.

1) Be sure to use shielded twisted pair cables and provided class 3 grounding.

2) Separate a twisted pair cable from power cables or I/O line that may generate noise.

3) Use a stabilized power supply for pulse generator.

▶ For 1-phase input, connect count-input signal only to phase A;

▶ For 2-phase input, connect to phases A and B.

### DC5V Output type encoder

OUT

20kΩ

GND

20kΩ

20kΩ

20kΩ

A24V

G4F-HO1A/G6F-HO1A

A12V

A5V

AB_COM

B24V

B12V

B5V

P24V

P12V

P5V

PG_COM

G24V

G12V

G5V

OUT0

OUT1

OUT2

OUT3

24V

24G

OUT

OUT

OUT

GND

GND

GND

5V DC

-

+

Encoder

L

L

24V DC

L

L

+

-

Phase A

Phase B

Preset

Gate

Twist Shield Cable

Twist Shield Cable

Twist Shield Cable

Twist Shield Cable

### DC12V NPN Open collector type encoder

OUT

12V

A24V

G4F-HO1A/G6F-HO1A

A12V

A5V

AB_COM

B24V

B12V

B5V

P24V

P12V

P5V

PG_COM

G24V

G12V

OUT

OUT

OUT

12V

12V

12V

Encoder

Phase A

Phase B

Preset

Gate

G5V

External source

12V DC

0V

Twist Shield Cable

Twist Shield Cable

Twist Shield Cable

Twist Shield Cable

+12V

0V

### DC24V PNP Open collector type encoder

G4F-HO1A/G6F-HO1A

OUT

0V

A12V

A5V

AB_COM

B24V

B12V

B5V

P24V

P12V

P5V

PG_COM

G12V

OUT

OUT

OUT

0V

0V

0V

Encoder

Phase A

Phase B

Preset

Gate

G5V

External source

24V DC

0V

Twist Shield Cable

Twist Shield Cable

Twist Shield Cable

Twist Shield Cable

A24V

G24V

+24V

0V

### Line driver type encoder

B-

B+

A-

VCC

VCC

Twist Shield Cable

A+

A-

A+

Twist Shield Cable

B+

B-

VCC

External source

VCC

0V

0V

G4F-HD1A/G6F-HD1A

Encoder