# Function block

■ This chapter describes function blocks for High-Speed Count Module.

| No | G4F-HO1A |  | G6F-HO1A |  | Description |
| --- | --- | --- | --- | --- | --- |
|  | G4F-HD1A |  | G6F-HD1A |  |  |
|  | Local | Remote | Local | Remote |  |
| 1 | HSCB_PRE | HSCB*RPR | HSCB_PRE | HSCB*RPR | Preset setting |
| 2 | HSCB_MOD | HSCB*RMD | HSCB_MOD | HSCB*RMD | Count mode and Linear/Ring count selection |
| 3 | HSCB_AUX | HSCB*RAX | HSCB_AUX | HSCB*RAX | Function setting |
| 4 | HSCB_CMP | HSCB*RCP | HSCB_CMP | HSCB*RCP | Coincidence output setting |
| 5 | HSCB_CNT | HSCB*RCT | HSCB_CNT | HSCB*RCT | Current count value reading |
| 6 | HSCB_WR | HSCB*RWR | HSCB_WR | HSCB*RWR | Operating information writing |
| 7 | HSCB_RD | HSCB*RRD | HSCB_RD | HSCB*RRD | Operating information reading |
| 8 | HSCB_OUT | HSCB*ROT | HSCB_OUT | HSCB*ROT | Coincidence output state reading |

## Insertion of the Function Block on the GMWIN

Function Block is inserted on the execution of the GMWIN according to following procedure.

Project (P)

■GMWIN V3.62 Example

Library insertion

G4F-HO1A, G4F-HD1A

- Special.4fb

- Remote3.4fb

- Remote4.4fb

G6F-HO1A, G6F-HD1A

- Special.6fb

- Remote3.6fb

- Remote4.6fb

- Remote6.6fb

## Local function block

### Preset setting function block (HSCB_PRE)

■ This function block sets the preset value.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH STAT DONE PSET HSCB_PRE | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel ● “0”: channel 0, “1”: channel 1 |
|  |  | PSET | DINT | Preset value ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number ● Indicates the error that occurs during execution of the function block. |

### Count mode setting function block(HSCB_MOD)

■ This function block sets the count mode and linear/ring count.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_MOD STAT DONE MODE SEL RING _L RING _H | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel ● “0”: channel 0, “1”: channel 1 |
|  |  | MODE | USINT | Count mode ● Range : 0 ∼ 7 Value; Description. 0; 2 phase multiple of 1. 1; 2 phase multiple of 2. 2; 2 phase multiple of 4. 3; CW/CCW. 4; 1 phase multiple of 1 (up/down count by program). 5; 1 phase multiple of 2 (up/down count by program). 6; 1 phase multiple of 1 (up/down count by phase B). 7; 1 phase multiple of 2 (up/down count by phase B). |
|  |  | SEL | BOOL | Linear / Ring count selection ● 0: Linear count ● 1: Ring count |
|  |  | RING_L | DINT | User-defined minimum value of Ring count ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  |  | RING_H | DINT | User-defined maximum value of Ring count ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number ● Indicates the error that occurs during execution of the function block. |

### Supplementary function setting function block (HSCB_AUX)

■ This function block sets the functions.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_AUX STAT DONE AUX SET_ TIME | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel ● “0”: channel 0, “1”: channel 1 |
|  |  | AUX | USINT | Function selection ● Range : 0 ∼ 5 Value; Description. 0; -. 1; Count clear function. 2; Count latch function. 3; Sampling count function. 4; Pulse frequency count function. 5; Periodic pulse count function. |
|  |  | SET_TIME | UINT | Preset time for sampling count function. ● Range : 1 ∼ 65,535 (ms) |
|  |  |  |  | Preset time for periodic pulse count function. ● Range : 1 ∼ 65,535 (ms) |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number ● Indicates the error that occurs during execution of the function block. |

### Coincidence output setting function block (HSCB_CMP)

■ This function block sets the coincidence output conditions and values.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_CMP STAT DONE CMPS CMPL CMPH | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel ● “0”: channel 0, “1”: channel 1 |
|  |  | CMPS | USINT [Array] *1 | Coincidence output selection ● Range : 0 ∼ 6 Value; Symbol; Description. 0; <; Less than. 1; ≤; Equal or less than. 2; =; Equal. 3; ≥; Equal or more than. 4; >; More than. 5; ≤ ≤; Including (for a section). 6; ≥ ≤; Not including (for a section). |
|  |  | CMPL | DINT [Array] *1 | Compared value for coincidence output selection 0~4 or User-defined minimum value for selection 5~6. ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  |  | CMPH | DINT [Array] *1 | User-defined maximum value for selection 5~6. ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number ● Indicates the error that occurs during execution of the function block. |

| Remark |  |
| --- | --- |
| ※1 : Number of array is 4. |  |

### Count reading function block (HSCB_CNT)

■ This function block reads the count value of the current and the function count.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_CNT STAT DONE CNT LTCH _OLD SCNT _NEW TIME _A TIME _B | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |
|  |  | CNT | DINT | Current count value. ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  |  | LTCH_OLD | DINT | Latched count value ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  |  |  |  | Previous count values for periodic pulse count function. ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  |  | SCNT_NEW | DINT | Sampling count value ● Range : 0 ∼ -2,147,483,648 or 0 ∼ +2,147,483,647 |
|  |  |  |  | Current count values for periodic pulse count function. ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  |  | TIME_A | UDINT | Number of phase A clock for pulse frequency count function. ● Range : 1 ∼ 25,000,000 (EA) |
|  |  | TIME_B | UDINT | Number of phase B clock for pulse frequency counts function. ● Range : 1 ∼ 25,000,000 (EA) |

### Operating information writing function block(HSCB_WR)

■ This function block writes Count enable command, Preset enable command, Up/down count enable command, Gate enable command etc to PLC.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_WR STAT DONE CNT_ E PRE_ E DOWN AUX_E CY_R PRE_ I/E AUX_ I/E PRE_ R AUX_ R | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | CNT_E | BOOL | Count enable command ● “0”: count enable. ● “1”: count disable. |
|  |  | PRE_E | BOOL | Preset enable command ● “0”: preset disable. ● “1”: preset enable. |
|  |  | DOWN | BOOL | Up/down count enable by program ● “0”: up count. ● “1”: down count. |
|  |  | AUX_E | BOOL | Function enable command. ● “0”: function disable ● “1 “: function enable. |
|  |  | CY_R | BOOL | Carry/ Borrow reset command. ● “0”: carry / borrow state is retained. ● “1”: carry / borrow is reset. |
|  |  | PRE_I/E | BOOL | Preset enable method selection (program or terminal input) ● “0”: preset enable by program. ● “1”: preset enable by terminal input. |
|  |  | AUX_I/E | BOOL | Function enable method selection (program or terminal input) ● “0”: preset enable by program. ● “1”: preset enable by terminal input |
|  |  | PRE_R | BOOL | Preset flag (occurred by terminal input) reset command ● “0”: preset flag is retained. ● “1”: preset flag is reset. |
|  |  | AUX_R | BOOL | Function flag (occurred by terminal input) reset command ● “0”: preset flag is retained. ● “1”: preset flag is reset. |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |

### Operating information reading function block (HSCB_RD)

■ This function block reads Carry, Borrow, Preset flag, Function flag etc from PLC.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_RD STAT DONE PRE_ F DOWN _F CY AUX_ F AUX_ ING BW | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |
|  |  | DOWN_F | BOOL | Up/down count flag ● “0”: up count ● “1”: down count |
|  |  | PRE_F | BOOL | Preset flag (occurred by terminal input) ● “0”: preset input is OFF (by terminal input) ● “1”: preset input is OFF (by terminal input) |
|  |  | AUX_F | BOOL | Function flag (occurred by terminal input) ● “0”: function input is OFF (by terminal input) ● “1”: function input is OFF (by terminal input) |
|  |  | CY | BOOL | Carry ● “0”: no carry occurred. ● “1”: carry occurred. |
|  |  | BW | BOOL | Borrow ● “0”: no borrow occurred. ● “1”: borrow occurred. |
|  |  | AUX_ING | BOOL | Function run signal ● “0”: function OFF. ● “1”: function ON. |

### Coincidence output function block(HSCB_OUT)

■ This function block writes Coincidence output enable command, Comparing enable command to PLC and reads coincidence output state from PLC.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB_OUT STAT DONE CMP_ E OUT_ E EQ0_R EQ1_R EQ2_R EQ3_R OUT0 OUT1 OUT2 OUT3 | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | CMP_E | BOOL | Comparing enable command. ● “0”: comparison disable. ● “1”: comparison enable. |
|  |  | OUT_E | BOOL | Coincidence output enable command. ● “0”: coincidence output disable of OUT0/OUT1/OUT2/OUT3 ● “1”: coincidence output enable of OUT0/OUT1/OUT2/OUT3 |
|  |  | EQ0_R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT0. ● “1”: coincidence output occurred by “equal” is reset. |
|  |  | EQ1_R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT1. ● “1”: coincidence output occurred by “equal” is reset. |
|  |  | EQ2_R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT2. ● “1”: coincidence output occurred by “equal” is reset. |
|  |  | EQ3_R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT3. ● “1”: coincidence output occurred by “equal” is reset. |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |
|  |  | OUT0 | BOOL | Coincidence output state of OUT0. ● “0”: coincidence output of OUT0 is OFF. ● “1”: coincidence output of OUT0 is ON. |
|  |  | OUT1 | BOOL | Coincidence output state of OUT1. ● “0”: coincidence output of OUT1 is OFF. ● “1”: coincidence output of OUT1 is ON. |
|  |  | OUT2 | BOOL | Coincidence output state of OUT2. ● “0”: coincidence output of OUT2 is OFF. ● “1”: coincidence output of OUT2 is ON. |
|  |  | OUT3 | BOOL | Coincidence output state of OUT3. ● “0”: coincidence output of OUT3 is OFF. ● “1”: coincidence output of OUT3 is ON. |

## Remote function block

### Preset setting function block (HSCB*RPR)

■ This function block sets the preset value.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*RPR8 ERR DONE PSET NET_ NO ST_N O STAT | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | PSET | DINT | Preset value ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |

### Count mode setting function block (HSCB*RMD)

■ This function block sets the count mode and linear/ring count.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*RMD ERR DONE MODE SEL RING _L RING _H NET_ NO ST_N O STAT | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | MODE | USINT | Count mode ● Range : 0 ∼ 7 Value; Description. 0; 2 phase multiple of 1. 1; 2 phase multiple of 2. 2; 2 phase multiple of 4. 3; CW/CCW. 4; 1 phase multiple of 1 (up/down count by program). 5; 1 phase multiple of 2 (up/down count by program). 6; 1 phase multiple of 1 (up/down count by phase B). 7; 1 phase multiple of 2 (up/down count by phase B). |
|  |  | SEL | BOOL | Linear / Ring count selection ● 0: Linear count ● 1: Ring count |
|  |  | RING_L | DINT | User-defined minimum value of Ring count ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  |  | RING_H | DINT | User-defined maximum value of Ring count ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |

### Function setting function block (HSCB*RAX)

■ This function block sets the functions.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*RAX ERR DONE AUX SET_ TIME STAT ST_N O NET_NO | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | AUX | USINT | Function selection ● Range : 0 ∼ 5 Value; Description. 0; -. 1; Count clear function. 2; Count latch function. 3; Sampling count function. 4; Pulse frequency count function. 5; Periodic pulse count function. |
|  |  | SET_TIME | UINT | Preset time for sampling count function. ● Range : 1 ∼ 65,535 (ms) |
|  |  |  |  | Preset time for periodic pulse count function. ● Range : 1 ∼ 65,535 (ms) |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |

### Coincidence output setting function block (HSCB*RCP)

■ This function block sets the coincidence output conditions and values.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*RCP STAT DONE CMPS CMPL CMPH NET_ NO ST_N O ERR | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | CMPS | USINT [Array] *1 | Coincidence output selection ● Range : 0 ∼ 6 Value; Symbol; Description. 0; <; Less than. 1; ≤; Equal or less than. 2; =; Equal. 3; ≥; Equal or more than. 4; >; More than. 5; ≤; Including (for a section). 6; ≥ ≤; Not including (for a section). |
|  |  | CMPL | DINT [Array] *1 | Compared value for coincidence output selection 0~4 or User-defined minimum value for selection 5~6. ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  |  | CMPH | DINT [Array] *1 | User-defined maximum value for selection 5~6. ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |

| Remark |  |
| --- | --- |
| ※1 : Number of array is 4. |  |

### Count reading function block (HSCB*RCT)

■ This function block reads the count value of the current and the function count.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*RCT STAT DONE CNT LTCH _OLD SCNT _NEW TIME _A TIME _B ERR NET_ NO ST_N O | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |
|  |  | CNT | DINT | Current count value. ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  |  | LTCH_OLD | DINT | Latched count value ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  |  |  |  | Previous count values for periodic pulse count function. ● Range: -2,147,483,648 ∼ 2,147,483,647 |
|  |  | SCNT_NEW | DINT | Sampling count value ● Range : 0 ∼ -2,147,483,648 or 0 ∼ +2,147,483,647 |
|  |  |  |  | Current count values for periodic pulse count function. ● Range : -2,147,483,648 ∼ 2,147,483,647 |
|  |  | TIME_A | UDINT | Number of phase A clock for pulse frequency count function. ● Range : 1 ∼ 25,000,000 (EA) |
|  |  | TIME_B | UDINT | Number of phase B clock for pulse frequency counts function. ● Range : 1 ∼ 25,000,000 (EA) |

### Operating information writing function block(HSCB*RWR)

■ This function block writes Count enable command, Preset enable command, Up/down count enable command, Gate enable command etc to PLC.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*RWR STAT DONE CNT_ E PRE_ E DOWN AUX_ E CY_R PRE_ I/E AUX_ I/E PRE_ R AUX_ R ERR NET_ NO ST_N O | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | CNT_E | BOOL | Count enable command ● “0”: count enable. ● “1”: count disable. |
|  |  | PRE_E | BOOL | Preset enable command ● “0”: preset disable. ● “1”: preset enable. |
|  |  | DOWN | BOOL | Up/down count enable by program ● “0”: up count. ● “1”: down count. |
|  |  | AUX_E | BOOL | Function enable command. ● “0”: function disable ● “1 “: function enable. |
|  |  | CY_R | BOOL | Carry/ Borrow reset command. ● “0”: carry / borrow state is retained. ● “1”: carry / borrow is reset. |
|  |  | PRE_I/E | BOOL | Preset enable method selection (program or terminal input) ● “0”: preset enable by program. ● “1”: preset enable by terminal input. |
|  |  | AUX_I/E | BOOL | Function enable method selection (program or terminal input) ● “0”: preset enable by program. ● “1”: preset enable by terminal input |
|  |  | PRE_R | BOOL | Preset flag (occurred by terminal input) reset command ● “0”: preset flag is retained. ● “1”: preset flag is reset. |
|  |  | AUX_R | BOOL | Function flag (occurred by terminal input) reset command ● “0”: preset flag is retained. ● “1”: preset flag is reset. |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |

### Operating information reading function block (HSCB*RRD)

■ This function block reads Carry, Borrow, Preset flag, Function flag etc from PLC.

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| BASE SLOT CH HSCB*RRD STAT DONE PRE_ F DOWN _F CY AUX_ F AUX_ ING BW NET_ NO REQ ST_N O ERR | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |
|  |  | DOWN_F | BOOL | Up/down count flag ● “0”: up count ● “1”: down count |
|  |  | PRE_F | BOOL | Preset flag (occurred by terminal input) ● “0”: preset input is OFF (by terminal input) ● “1”: preset input is OFF (by terminal input) |
|  |  | AUX_F | BOOL | Function flag (occurred by terminal input) ● “0”: function input is OFF (by terminal input) ● “1”: function input is OFF (by terminal input) |
|  |  | CY | BOOL | Carry ● “0”: no carry occurred. ● “1”: carry occurred. |
|  |  | BW | BOOL | Borrow ● “0”: no borrow occurred. ● “1”: borrow occurred. |
|  |  | AUX_ING | BOOL | Function run signal ● “0”: function OFF. ● “1”: function ON. |

### Coincidence output function block(HSCB*ROT)

■ This function block writes Coincidence output enable command, Comparing enable command to PLC and reads coincidence output state from PLC..

| Figure | I/O | Variable name | Data type | Description |
| --- | --- | --- | --- | --- |
| REQ BASE SLOT CH HSCB*ROT STAT DONE CMP_ E OUT_ E EQ0_R EQ1_R EQ2_R EQ3_R OUT0 OUT1 OUT2 OUT3 ERR NET_ NO ST_N O ` | Input | REQ | BOOL | Function block execution request. ● When this variable is turned “0→1” function block is executed. |
|  |  | NET_NO | USINT | Slot No. (0 ~ 7) of the local communication modules (G3L – FUEA, G4L – FUEA, G3L – FUOA) are mounted. ● Range : 0 ∼ 7 |
|  |  | ST_NO | USINT | Station No. (0 ~ 63) of the communication modules (G3L – RBEA, G4L – RBOA, G4L – BBEA) mounted on the remote I/O station. ● Range : 0 ∼ 63 |
|  |  | BASE | USINT | Base location No. ● Number of base that high-speed counter module is mounted. ● Range : GM4 series(0 ∼ 3), GM6 series : 0 |
|  |  | SLOT | USINT | Slot location No. ● Number of slot that high-speed counter module is mounted. ● Range : 0 ∼ 7 |
|  |  | CH | BOOL | Channel. ● “0”: channel 0, “1”: channel 1 |
|  |  | CMP_E | BOOL | Comparing enable command. ● “0”: comparison disable. ● “1”: comparison enable. |
|  |  | OUT_E | BOOL | Coincidence output enable command. ● “0”: coincidence output disable of OUT0/OUT1/OUT2/OUT3 ● “1”: coincidence output enable of OUT0/OUT1/OUT2/OUT3 |
|  |  | EQ0R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT0. ● “1”: coincidence output occurred by “equal” is reset. |
|  |  | EQ1R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT1. ● “1”: coincidence output occurred by “equal” is reset. |
|  |  | EQ2R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT2. ● “1”: coincidence output occurred by “equal” is reset. |
|  |  | EQ3R | BOOL | Coincidence output (occurred by “equal”) reset command for OUT3. ● “1”: coincidence output occurred by “equal” is reset. |
|  | Output | DONE | BOOL | Function block execution signal ● If this function block is executed without error, DONE is “1” and the opposite case “0”. |
|  |  | ERR | BOOL | Error state of function block execution ● Turns ON If error occurs during the execution of the function block |
|  |  | STAT | USINT | Error number. ● Indicates the error that occurs during execution of the function block. |
|  |  | OUT0 | BOOL | Coincidence output state of OUT0. ● “0”: coincidence output of OUT0 is OFF. ● “1”: coincidence output of OUT0 is ON. |
|  |  | OUT1 | BOOL | Coincidence output state of OUT1. ● “0”: coincidence output of OUT1 is OFF. ● “1”: coincidence output of OUT1 is ON. |
|  |  | OUT2 | BOOL | Coincidence output state of OUT2. ● “0”: coincidence output of OUT2 is OFF. ● “1”: coincidence output of OUT2 is ON. |
|  |  | OUT3 | BOOL | Coincidence output state of OUT3. ● “0”: coincidence output of OUT3 is OFF. ● “1”: coincidence output of OUT3 is ON. |

## Error code on the function block

■ The errors on the output variable “STAT” of function blocks and the resolutions in accordance with them is shown below

| STAT No. | Local/ Remote | Descriptions | Resolutions |
| --- | --- | --- | --- |
| 0 | Local | Operating with no fault | - |
| 1 |  | The base number is not within the proper setting range. | Correct the base number within the proper range. |
| 2 |  | H/W error of the base | Contact with the service station. |
| 3 |  | The slot number is not within the proper setting range | Correct the slot number within the proper range. |
| 4 |  | The slot is empty | Mount the high speed counter module to the slot |
| 5 |  | The module loaded isn't the high speed counter module | Mount the high speed counter module to the slot |
| 6 |  | - | - |
| 7 |  | H/W error of the high speed counter module | Contact with the service station. |
| 8 |  | The high speed counter module's shared memory error | Contact with the service station. |
| 9 |  | - | - |
| 128 | Remote | H/W error of the communication module for remote | See the manual of the remote communication module |
| 129 |  | The base location number is not within the proper setting range | Correct the number within the proper range. |
| 131 |  | The slot location number is not within the proper setting range | Correct the number within the proper range. |
| 133 |  | Another module is mounted on the selected slot. | Mount the high-speed counter module to the slot. |
| 135 |  | H/W error of the high speed counter module | Contact with the service station. |
| 136 |  | The high speed counter module's shared memory error | Contact with the service station. |
| 137 |  | The channel number is not within the range. | Correct the channel number within the range. |