#### Chapter 11 Trouble Shooting

Here describes the contents of each error to be occurred while operating the system, the method to find the cause and the action.

11.1 Basic Procedure of Trouble Shooting

It is important to use the high reliable machine to increase the system reliability but it is important to take a prompt action when the trouble occurs as well.

To start the system promptly, it is more important to find the trouble occurring cause promptly and take the necessary action. The basic items to comply when taking this trouble shooting are as follows.

1)  Check by the naked eye

Check the following items by the naked eye.

 Machine action status (stop, action)

 Power appliance status

 I/O machine status

 Wiring status (I/O cable, extended or communication cable)

 Check the indication status of each indicator (POWER LED, RUN LED, ERR LED, TX LED,RX LED, MS LED,NS LED, I/O LED etc.) and connect the peripheral device and then check the PLC action status or the program contents.

2)  Check the trouble

Examine how the trouble is changed by the following action.

 Place the key switch on STOP position and apply the power ON/OFF.

3)  Limit range

Estimate what is the trouble cause using the above method.

  Is it the cause from PLC itself? Or external cause?

  Is it the cause from I/O part? Or other cause?

  Is it the cause from PLC program?

11.2 Trouble Shooting

Here describes the trouble finding method, the error code and the actions on the above by dividing them per phenomenon.

Description of Trouble

When POWER LED is OFF

Action method when POWER LED is OFF.

When ERR LED is blinking

Action method when ERR LED is blinking.

When RUN LED is OFF.

Action method when RUN LED is OFF.

In case of abnormal operation I/O part

Action method in case of abnormal operation of I/O part

When program write does not work

Action method when program write does not work.

11.2.1 Action method when POWER LED is OFF.

Here describes the action order when POWER LED is OFF while apply the power or during the operation.

POWER LED is OFF

Yes

Is the power supplying?

No

Yes

Supply the power.

Is POWER LED ‘ON’?

Meet the supply power within the regular range.

Connect power cable completely.

No

Yes

Is the power voltage within the allowable range?

No

Yes

No

Is POWER LED ‘ON’?

No

Is the power cable connected well?

Yes

1) Check the current capacity and reduce the over current..

2) After input power OFF, then power ON.

Is the over current protection acting?

No

No

Yes

Yes

Is POWER LED

‘ON’?

After writing the trouble shooting questionnaire, contact the customer center

End

11.2.2 Action method when ERR LED is blinking.

Here describes the action order when ERR LED is blinking in case of the power input, or when operation start, or during operation.

ERR LED is blinking.

Connect GMWIN and check the error code contents.

Is it warning error (_CNF_WAR) ?

Yes

Refer to typical system warning flag and remove the trouble cause.

No

Yes

Is ERR  LED keeping

on blinking ?

No

After writing the trouble shooting questionnaire and contact the customer center.

End

11.2.3 Action method when RUN LED is OFF

Here describes the action order when RUN LED is blinking in case of the power input, or when operation start, or during operation.

RUN LED is OFF

After the power unit OFF, apply it ON.

No

Is RUN LED ‘OFF’?

Yes

End

Contact to the customer center.

11.2.4 Action method when I/O part does not work normally.

Here describes the action order when I/O part does not work normally during operation, as shown on the program example below.

When I/O part does not work normally,

Is output LED of SOL1

‘ON’?

No

Yes

Monitor SOL1 status by GMWIN.

Change the connector of terminal stand.

Measure SOL1 terminal voltage by the tester.

Make the correct wiring.

No

No

No

Yes

Is the measured value

normal?

Is the output wiring

correct?

Is the contact status of terminal stand connector good?

Is it normal?

Yes

No

Yes

Yes

After removing the external wiring, check the monitoring status of output part.

Yes

No

Cont’d계속

Is it normal?

Check the output

machine(SOL1) status.

Change the unit.

Continuance

Is SWITCH1, 2 LED

‘ON’?

No

Yes

Measure the terminal voltage of SWITCH1, 2 by the tester.

Measure the terminal voltage of SWITCH1, 2 by the tester.

Yes

Is the measured value

normal?

Is the measured value

normal?

Is the tightening

status of terminal

good?

No

No

No

Yes

Yes

Is input wiring correct?

Is the contact

status of terminal stand

connector good?

Yes

No

No

After removing the external

wiring, check the input

status by the forced input.

Is the measured value

normal?

Make the correct wiring.

Tighten the terminal screw completely.

Change the terminal stand connector.

No

Yes

Check all from the beginning again.

Check the input machine (SWITCH1, 2).

Change the unit.

Change the unit.

11.2.5 Action method when Program Write does not work

Here describes the action order when Program write does not work in the Master CPU.

Program write does not work

Put the key switch to remote STOP mode and run Program write.

No

Is the key switch set as remote STOP mode?

Yes

After reading the error code by using the peripherals, correct it according to the contents.

Yes

Is ERR. LED

blinking?

End

11.3 Trouble Shooting Questionnaire

If the trouble occurs when using SMART I/O series, fill in the following questionnaire and contact to the customer center by phone or by fax.

 In case of error related to specific and communication module, use the questionnaire added to the user’s manual of the corresponding product.

1. User contact point :                     TEL.)

FAX)

2. Model :                               (    )

3. Applied machine details

 Network status :          OS version (          ),       Serial no. of product  (           )

 GMWIN  version no. used in program compile  : (           )

4. brief description of control object machine and system :

5. Network model using :

6. ERR  LED ‘OFF’ of network unit?     Yes(         ),  No(         )

7. Error message content by GMWIN :

8. Action trial status for the error code. :

9. Trouble shooting method for other error action :

10. Error features

 Repeat(      ) : periodical(      ) ,  specific sequence level related(       )

environment related(       )

 Intermittent(      ) : error interval :

12. Detail description for the error phenomena :

13. Configuration diagram of applied system: