Chapter 3 System Configuration

Smart I/O series is equipped with various product suitable for system configuration as various communication models and I/O module. This chapter describes the method of system configuration and characteristics.

3.1 Notices in Selecting Module

Here describes the notices in selecting digital I/O module which is used for Remote I/O.

1) Digital input types contain the current sink input and current source input. In case of DC input module, as the wiring method of external input power is different according to such input types, make sure of selecting the input module considering the spec. of input connection machine. Remote I/O is available for source/sink in common. The wiring method per type is as follows.

(1) How to connect the sink type external connection machine to the source type DC input module.

I

－

DC input

module

External connection

machine

DC power

＋

COM

 External connection machine is located between DC power and (-) terminal of DC input module terminal.

 Thus, when input ON, the current flows from DC input module terminal to external connection machine.

(2) How to connect the source type external connection machine to the sink type DC input module.

I

＋

DC input

module

External connection

machine

DC power

－

COM

－

 External connection machine is located between DC power and (+) terminal of DC input module terminal.

 Thus, when input ON, the current flows from external connection machine to DC input module terminal.

2) In case that the open/close frequency is high or it is used to open/close the conductive load, please use transistor output module as Relay output module may reduce the life.

3.2 Names of Each Part

3.2.1 Basic System Configuration

Smart I/O series contains all 4 kinds of module configuration. According to network configuration that the user wants, it is available to install the system simple and effectively by the combination of the following models. The best advantage of Smart I/O series is the simple system configuration and the easy connection with other maker’s machine as this is oriented to the open type network (except Rnet).

Example of Smart I/O Series Form

Available modules per network of Smart I/O series (I/O module)

| I/O configuration available point |  | 16 points or 32 points |
| --- | --- | --- |
| Product type | Profibus-DP Communication module |  GPL-TR2A / GPL-TR4A / GPL-RY2A  GPL-D22A / GPL-D24A  GPL-DT4A |
|  | DeviceNet Communication module |  GDL-TR2A / GDL-TR4A / GDL-RY2A  GDL-D22A / GDL-D24A  GDL-DT4A |
|  | Rnet Communication module |  GRL-TR2A / GRL-TR4A / GRL-RY2A  GRL-D22A / GRL-D24A  GRL-DT4A |
|  | Modbus Communication module |  GSL-TR2A / GSL-TR4A / GSL-RY2A  GSL-D22A / GSL-D24A  GSL-DT4A |

3.2.2 Names of Each Part of Smart I/O series

3.2.2.1 Profibus-DP, Rnet, Modbus series

Profibus-DP, Rnet, Modbus communication module has all same forms and their characteristics are as follows.

In case of I/O 16 points

①

②

③

④

⑦

⑤

⑥

In case of I/O 32 points,

④

①

②

③

⑥

⑦

⑤

1) Profibus-DP module

| No. | Item |  | Dscription |
| --- | --- | --- | --- |
| ① | Connection connector |  | Connector for communication connection with master/remote unit  9 pin connector |
| ② | Smart I/O type name indication |  |  Describes Profibus-DP module type name. GPL-D22A : DC input 16 points GPL-D24A : DC input 32 points GPL-TR2A : TR output 16 points GPL-TR4A : TR output 32 points GPL-RY2A : Relay output 16 points GPL-DT4A : DC input 16 points /TR output 16 points combined |
| ③ | Communi- cation status indication LED | RUN LED | It describes the status of power to be supplied to the system.  On : in case of normal power supply  Off : in case of abnormal power supply |
|  |  | RDY LED |  ON : when communication module is working normally. |
|  |  | ERR LED |  ON : when communication module is cut off. |
| ④ | station no. of its own station setting switch |  | The switch to set the node station no. of its own station. Available to set from 0~99 (‘0 ‘station reserved)  X10 : 10 digits indicated  X1 : 1 digit indicated |
| ⑤ | I/O LED |  | It describes the contact status of I/O terminal. |
| ⑥ | Hook for DIN rail attachment |  |  Hook for DIN rail attachment |
| ⑦ | Terminal block |  |  Terminal block layout for I/O wiring * Refer to Art.3.3. |

2) Rnet module

| No. | Item |  | Dscription |
| --- | --- | --- | --- |
| ① | Connection connector |  | Connector for communication connection with master/remote unit  9 pin connector |
| ② | Smart I/O type name indication |  |  Describes Rnet module type name. GRL-D22A : DC input 16 points GRL-D24A : DC input 32 points GRL-TR2A : TR output 16 points GRL-TR4A : TR output 32 points GRL-RY2A : Relay output 16 points GRL-DT4A : DC input 16 points/TR output 16 points combined |
| ③ | Communi-cation status indication LED | PWR LED | It describes the status of power to be supplied to the system.  On : in case of normal power supply  Off : in case of abnormal power supply |
|  |  | TX LED | It describes the transmission status of communication module.  Blink : when communication module is transmitting (except GRL-TR4A)  OFF : LED is OFF in the cases as follows ; ▶ in case that the voltage is not supplied normally to the basic unit. ▶ in case that the error to stop the operation is detected. |
|  |  | RX LED | It describes the receiving status of communication module.  Blink : when communication module is receiving.  Off : when communication module has no receiving or the error is detected. |
| ④ | Station no. of its own station setting switch |  | The switch to set the node station no. of its own station. Available to set from 0~63.  X16 : 16 digits indicated  X1 : 1 digit indicated |
| ⑤ | I/O LED |  | Describes the contact status of I/O terminal. |
| ⑥ | Hook for DIN rail attachment |  |  Hook for DIN rail attachment |
| ⑦ | Terminal block |  |  Terminal block layout for I/O wiring. * Refer to Art. 3.3. |

3) Modbus module

| No. | Item |  | Dscription |
| --- | --- | --- | --- |
| ① | Connection connector |  | Connector for communication connection with master/remote unit  9 pin connector |
| ② | Smart I/O type name indication |  |  Describes Modbus module type name. GSL-D22A : DC input 16 points GSL-D24A : DC input 32 points GSL-TR2A : TR output 16 points GSL-TR4A : TR output 32 points GSL-RY2A : Relay output 16 points GSL-DT4A : DC input 16 points/TR output 16 points combined |
| ③ | Communi-cation status indication LED | PWR LED | It describes the status of power to be supplied to the system.  On : in case of normal power supply  Off : in case of abnormal power supply |
|  |  | TX LED | It describes the transmission status of communication module.  Blink : when communication module is transmitting (except GRL-TR4A)  OFF : LED is OFF in the cases as follows ; ▶ in case that the voltage is not supplied normally to the basic unit. ▶ in case that the error to stop the operation is detected. |
|  |  | RX LED | It describes the receiving status of communication module.  Blink : when communication module is receiving.  Off : when communication module has no receiving or the error is detected. |
| ④ | Station no. of its own station setting switch |  | The switch to set the node station no. of its own station. Available to set from 0~31.  X16 : 16 digits indicated  X1 : 1 digit indicated |
| ⑤ | I/O LED |  | It describes the contact status of I/O terminal. |
| ⑥ | Hook for DIN rail attachment |  |  Hook for DIN rail attachment |
| ⑦ | Terminal block |  |  Terminal block layout for I/O wiring * Refer to Art. 3.3. |

3.2.2.2 DeviceNet Series

The form of DeviceNet communication module is as follows.

In case of I/O 16 points,

①

②

③

④

⑤

⑥

In case of I/O 32 points,

④

①

②

③

⑥

⑤

1) DeviceNet module

| No. | Item |  | Dscription |
| --- | --- | --- | --- |
| ① | Connection connector |  | Connector for communication connection with master/remote unit  5 pin OPEN type connector |
| ② | Smart I/O type name indication |  |  Describes DeviceNet module type name. GDL-D22A : DC input 16 points GDL-D24A : DC input 32 points GDL-TR2A : TR output 16 points GDL-TR4A : TR output 32 points GDL-RY2A : Relay output 16 points GDL-DT4A : DC input 16 points/TR output 16 points combined |
| ③ | Communi- cation status indication LED | PWR LED | It describes the status of power to be supplied to the system.  On : in case of normal power supply  Off : in case of abnormal power supply |
|  |  | MS LED | It describes interface status of communication module.  Blink : when communication module is in normal interface with CPU.  OFF : Interface error |
|  |  | NS LED | It describes network status of communication module.  Blink : when it is in normal interface with other machine. |
| ④ | Station no. of its own station setting switch |  | The switch to set the node station no. of its own station. Available to set from 0~63.  X16 : 16 digits indicated  X1 : 1 digit indicated |
| ⑤ | I/O LED |  | It describes the contact status of I/O terminal. |
| ⑥ | Hook for DIN rail attachment |  |  Hook for DIN rail attachment |
| ⑦ | Terminal block |  |  Terminal block layout for I/O wiring * Refer to Art. 3.3. |

3.3 I/O Wiring Diagram of Communication Module

3.3.1 External connection diagram of Smart I/O module

3.3.1.1 Profibus-DP module

1) Terminal block configuration

| Terminal block |  | Contact and Power Input |
| --- | --- | --- |
| GPL-D22A / GPL-D24A | 0 ~ 15 | Input contact terminal (GPL-D22A) |
|  | 0 ~ 31 | Input contact terminal (GPL-D24A) |
|  | COM | Common terminal(16 points COM)(GPL-D22A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GPL-D24A) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |
| GPL-DT4A | 0 ~ 15/0 ~ 15 | I/O contact terminal |
|  | COM0/COM1 | Common terminal(16 points COM) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |
| GPL-TR2A / GPL-TR4A | 0 ~ 15 | Output contact terminal(GPL-TR2A) |
|  | 0 ~ 31 | Output contact terminal(GPL-TR4A) |
|  | COM | Common terminal(16 points COM)(GPL-TR2A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GPL-TR4A) |
|  | FG | FG terminal |
|  | 24V | DC 24V(+) power input terminal |
|  | 24G | DC 24V(-) power input terminal |
| GPL-RY2A | 0 ~ 15 | Output contact terminal |
|  | COMA~COMD | Common terminal(8 points COM) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |

2) Wiring Diagram

| Classifi-cation | Wiring Diagram |
| --- | --- |
| COM 15 13 11 09 07 05 03 01 DC 24G DC 24V . COM 14 12 10 08 06 04 02 00 FG COM1 30 18 16 15 03 01 DC 24G DC 24V . 31 19 17 COM0 04 02 00 FG 15 13 11 09 07 05 03 01 DC 24G DC 24V COM1 14 12 10 08 06 04 02 00 FG DC input module | [GPL-D22A] [GPL-D24A] [GPL-DT4A(input section)] |
| COM 15 13 11 09 07 05 03 01 DC 24G DC 24V DC 24V COM 14 12 10 08 06 04 02 00 FG COM1 30 18 16 15 03 01 DC 24G DC 24V DC 24V 31 19 17 COM0 04 02 00 FG COM1 COM0 14 12 10 08 06 04 02 00 FG 15 DC 24V 15 13 11 09 07 05 03 01 DC 24G DC 24V TR output module | [GPL-TR2A] [GPL-TR4A] [GPL-DT4A(Output section)] |
| . . . . . . . . . 00 COMA COMA COMB 03 04 07 08 COMC COMC COMD 11 12 15 01 02 06 COMA COMA 05 COMA 09 10 14 COMC COMC 13 COMC . RELAY Output module | [GPL-RY2A] * COMA and COMB are connected internally respectively. |

3.3.1.2 DeviceNet module

1) Terminal block configuration

| Terminal block |  | Contact and Power Input |
| --- | --- | --- |
| GDL-D22A / GDL-D24A | 0 ~ 15 | Input contact terminal(GDL-D22A) |
|  | 0 ~ 31 | Input contact terminal(GDL-D24A) |
|  | COM | Common terminal(16 points COM)(GDL-D22A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GDL-D24A) |
| GDL-DT4A | 0 ~ 15/0 ~ 15 | I/O contact terminal |
|  | COM0/COM1 | Common terminal(16 points COM) |
| GDL-TR2A / GDL-TR4A | 0 ~ 15 | Output contact terminal(GDL-TR2A) |
|  | 0 ~ 31 | Output contact terminal(GDL-TR4A) |
|  | COM | Common terminal(16 points COM)(GDL-TR2A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GDL-TR4A) |
| GDL-RY2A | 0 ~ 15 | Output contact terminal |
|  | COMA~COMD | Common terminal(8 points COM) |

2) Wiring diagram

| Classifi- cation | Wiring diagram |
| --- | --- |
| COM 15 13 11 09 07 05 03 01 . COM 14 12 10 08 06 04 02 00 COM1 30 18 16 15 03 01 . 31 19 17 COM0 04 02 00 15 13 11 09 07 05 03 01 COM1 14 12 10 08 06 04 02 00 DC input module | [GDL-D22A] [GDL-D24A] [GDL-DT4A(input section)] |
| COM 15 13 11 09 07 05 03 01 DC 24V COM 14 12 10 08 06 04 02 00 COM1 30 18 16 15 03 01 DC 24V 31 19 17 COM0 04 02 00 COM1 COM0 14 12 10 08 06 04 02 00 15 DC 24V 15 13 11 09 07 05 03 01 TR output module | [GDL-TR2A] [GDL-TR4A] [GDL-DT4A(output section)] |
| . . . . . . . . . 00 COMA COMA COMB 03 04 07 08 COMC COMC COMD 11 12 15 01 02 06 COMA COMA 05 COMA 09 10 14 COMC COMC 13 COMC . RELAY Output module | [GDL-RY2A] * COMA and COMB are connected internally respectively. |

3.3.1.3 Rnet module

1) Terminal block configuration

| Terminal block |  | Contact and Power Input |
| --- | --- | --- |
| GRL-D22A / GRL-D24A | 0 ~ 15 | Input contact terminal(GRL-D22A) |
|  | 0 ~ 31 | Input contact terminal(GRL-D24A) |
|  | COM | Common terminal(16 points COM)(GRL-D22A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GRL-D24A) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |
| GRL-DT4A | 0 ~ 15/0 ~ 15 | I/O contact terminal |
|  | COM0/COM1 | Common terminal(16 points COM) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |
| GRL-TR2A / GRL-TR4A | 0 ~ 15 | Output contact terminal(GRL-TR2A) |
|  | 0 ~ 31 | Output contact terminal(GRL-TR4A) |
|  | COM | Common terminal(16 points COM)(GRL-TR2A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GRL-TR4A) |
|  | FG | FG terminal |
|  | 24V | DC 24V(+) power input terminal |
|  | 24G | DC 24V(-) power input terminal |
| GRL-RY2A | 0 ~ 15 | Output contact terminal |
|  | COMA~COMD | Common terminal(8 points COM) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |

2) Wiring diagram

| Classifi- cation | Wiring diagram |
| --- | --- |
| COM 15 13 11 09 07 05 03 01 DC 24G DC 24V . COM 14 12 10 08 06 04 02 00 FG COM1 30 18 16 15 03 01 DC 24G DC 24V . 31 19 17 COM0 04 02 00 FG 15 13 11 09 07 05 03 01 DC 24G DC 24V COM1 14 12 10 08 06 04 02 00 FG DC input module | [GRL-D22A] [GRL-D24A] [GRL-DT4A(input section)] |
| COM 15 13 11 09 07 05 03 01 DC 24G DC 24V DC 24V COM 14 12 10 08 06 04 02 00 FG COM1 30 18 16 15 03 01 DC 24G DC 24V DC 24V 31 19 17 COM0 04 02 00 FG COM1 COM0 14 12 10 08 06 04 02 00 FG 15 DC 24V 15 13 11 09 07 05 03 01 DC 24G DC 24V TR output module | [GRL-TR2A] [GRL-TR4A] [GRL-DT4A(output section)] |
| . . . . . . . . . 00 COMA COMA COMB 03 04 07 08 COMC COMC COMD 11 12 15 01 02 06 COMA COMA 05 COMA 09 10 14 COMC COMC 13 COMC . RELAY Output module | [GRL-RY2A] * COMA and COMB are connected internally respectively. |

3.3.1.4 Modbus module

1) Terminal block configuration

| Terminal block |  | Contact and Power Input |
| --- | --- | --- |
| GSL-D22A / GSL-D24A | 0 ~ 15 | Input contact terminal(GSL-D22A) |
|  | 0 ~ 31 | Input contact terminal(GSL-D24A) |
|  | COM | Common input(16 points COM)(GSL-D22A) |
|  | COM0/COM1 | Common input(16 points COM)(GSL-D24A) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |
| GSL-DT4A | 0 ~ 15/0 ~ 15 | I/O contact terminal |
|  | COM0/COM1 | Common terminal(16 points COM) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |
| GSL-TR2A / GSL-TR4A | 0 ~ 15 | Output contact terminal(GSL-TR2A) |
|  | 0 ~ 31 | Output contact terminal(GSL-TR4A) |
|  | COM | Common terminal(16 points COM)(GSL-TR2A) |
|  | COM0/COM1 | Common terminal(16 points COM)(GSL-TR4A) |
|  | FG | FG terminal |
|  | 24V | DC 24V(+) power input terminal |
|  | 24G | DC 24V(-) power input terminal |
| GSL-RY2A | 0 ~ 15 | Output contact terminal |
|  | COMA~COMD | Common terminal(8 points COM) |
|  | FG | FG terminal |
|  | DC 24V | DC 24V(+) power input terminal |
|  | DC 24G | DC 24V(-) power input terminal |

2) Wiring diagram

| Classifi- cation | Wiring diagram |
| --- | --- |
| DC input module | COM 15 13 11 09 07 05 03 01 DC 24G DC 24V . COM 14 12 10 08 06 04 02 00 FG COM1 30 18 16 15 03 01 DC 24G DC 24V . 31 19 17 COM0 04 02 00 FG 15 13 11 09 07 05 03 01 DC 24G DC 24V COM1 14 12 10 08 06 04 02 00 FG [GSL-D22A] [GSL-D24A] [GSL-DT4A(input section)] |
| TR output module | COM 15 13 11 09 07 05 03 01 DC 24G DC 24V DC 24V COM 14 12 10 08 06 04 02 00 FG COM1 30 18 16 15 03 01 DC 24G DC 24V DC 24V 31 19 17 COM0 04 02 00 FG COM1 COM0 14 12 10 08 06 04 02 00 FG 15 DC 24V 15 13 11 09 07 05 03 01 DC 24G DC 24V [GSL-TR2A] [GSL-TR4A] [GSL-DT4A(output section)] |
| RELAY Output module | [GSL-RY2A] . . . . . . . . . 00 COMA COMA COMB 03 04 07 08 COMC COMC COMD 11 12 15 01 02 06 COMA COMA 05 COMA 09 10 14 COMC COMC 13 COMC . * COMA and COMB are connected internally respectively. |

3.4 Examples of System Configuration

3.4.1 Profibus-DP System

GMWIN

GM7

G7L-PBEA

Smart I/O

GPL-RY2A

GPL-D24A

GPL-DT4A

GPL-TR4A

Smart I/O

GPL-D22A

GPL-TR2A

GLOFA GM3

G3L-PUEA/PUEB

GLOFA GM4

G4L-PUEA/PUEB

GLOFA GM6

G6L-PUEA/PUEB

타사 PLC

CNC

3.4.2  DeviceNet System

GMWIN

GM7

G7L-DBEA

Smart I/O

GDL-RY2A

GDL-D24A

GDL-DT4A

GDL-TR4A

Smart I/O

GDL-D22A

GDL-TR2A

GLOFA GM4

G4L-DUEA

GLOFA GM6

G6L-DUEA

LG inverter

GLOFA GM4

G4L-DUEA

GLOFA GM6

G6L-DUEA

AB, OMRON

DeviceNet

Configurator S/W

LG inverter

AB Flex I/O

OMRON

3.4.3 Rnet System

GMWIN

GM7

G7L-RUEA

Smart I/O

GRL-RY2A

GRL-D24A

GRL-DT4A

GRL-TR4A

Smart I/O

GRL-D22A

GRL-TR2A

GLOFA GM3

G3L-RUEA

GLOFA GM4

G4L-RUEA

GLOFA GM6

G6L-RUEA

Smart I/O

GRL-RY2A

GRL-D24A

GRL-DT4A

GRL-TR4A

Smart I/O

GRL-D22A

GRL-TR2A

Smart I/O

GRL-RY2A

GRL-D24A

GRL-DT4A

GRL-TR4A

Smart I/O

GRL-D22A

GRL-TR2A

Smart I/O

GRL-RY2A

GRL-D24A

GRL-DT4A

GRL-TR4A

Smart I/O

GRL-D22A

GRL-TR2A

3.4.4 Modbus System

GMWIN

GM7

G7L-CUEC

Smart I/O

GSL-RY2A

GSL-D24A

GSL-DT4A

GSL-TR4A

Smart I/O

GSL-D22A

GSL-TR2A

GLOFA GM3

G3L-CUEA

GLOFA GM4

G4L-CUEA

GLOFA GM6

G6L-CUEC

Smart I/O

GSL-RY2A

GSL-D24A

GSL-DT4A

GSL-TR4A

Smart I/O

GSL-D22A

GSL-TR2A

Smart I/O

GSL-RY2A

GSL-D24A

GSL-DT4A

GSL-TR4A

Smart I/O

GSL-D22A

GSL-TR2A

Smart I/O

GSL-RY2A

GSL-D24A

GSL-DT4A

GSL-TR4A

Smart I/O

GSL-D22A

GSL-TR2A