Chapter 4. Variable of GLOFA-GM series

The variable includes the data value in the program. The variable indicates PLC I/O, internal memory and etc.

4.1.1.	Representation

▷	The variable is expressed by two types; one is by assigning name with identifier and the other is by expressing PLC I/O or physical or logical place in the memory in the data element directly.

▷	The variable by identifier shall be unique in the scope(program configuration region declared as variable) to identify other variable.

▷	Direct variable can be expressed by the order of prefix starting with % letter and data. The prefix is described as below.

Location prefix

| No. | Prefix | Meaning |
| --- | --- | --- |
| 1 | I | Input Location |
| 2 | Q | Output Location |
| 3 | M | Memory Location |

Size prefix

| No. | Prefix | Meaning |
| --- | --- | --- |
| 1 | X | Single bit size |
| 2 | None | Single bit size |
| 3 | B | Byte(8 Bits) size |
| 4 | W | Word(16 bits) size |
| 5 | D | Double Word(32 Bits) size |
| 6 | L | Long Word(64 Bits) size |

Expression type

%[Location prefix][Size prefix] n1.n2.n3

| No. | I, Q | M |
| --- | --- | --- |
| n1 | Base number(start from 0) | n1 data according to [Size prefix] (start from 0) |
| n2 | Slot number(start from 0) | n2 bit on n1 data (start from 0) : can be omitted. |
| n3 | n3 data according to [Size prefix] (start from 0) | Not used. |

Ex)

%QX3.1.4 or %Q3.1.4  : No. 4 output (1 Bit) of No. 1 slot of No. 3 base

%IW2.4.1	 :  No.1 input by the word unit of No. 4 slot of No. 2 base (16 Bits)

%MD48	:  Memory of double word unit located at 48

%MW40.3 :  No.3 bit in memory on word unit located at 40

(There is no concept of base, slot and etc. internal memory.)

▷	Small letter can not be used for the prefix.

▷	If size prefix is not used, the variable is processed as 1 bit.

▷	Direct variable can be used without declaration.

4.1.2.	Variable declaration

▷	Program configuration element(i.e. programn block, function, function block) has the declaration, which can declare the variable in configuration element.

▷	The variable shall be declared in order to use it in the program configuration element.

▷	Bellows shall be set for the variable declaration.

| Variable type | Description |
| --- | --- |
| VAR | General variable readable and writable |
| VAR_RETAIN | Retentive variable |
| VAR_CONSTANT | Variable readable only |
| VAR_EXTERNAL | Declaration to use VAR_GLOBAL variable |

Reference

Resource global variable and configuration global variable are declared by VAR_GLOBAL, VAR_GLOBAL_RETAIN, VAR_GLOBAL_CONSTANT and VAR_EXTERNAL can not be declared.

1)	Variable type : set how to declare the variable.

2)	Data type : Assign the data type of variable.

3)	Memory allocation : Allocate the memory for variable.
Automatic  ---- The compiler assigns the variable location automatically
		(Automatic allocation variable).
User definition(AT) ---- The user assigns the location by direct variable.
		      (Direct variable)

Reference

The location of automatic allocation variable is not fixed. For example, if VAL1 variable is declared as BOOL data type, the variable is not fixed in certain location in the data region. The compiler and linker define the location after programming. In case of compiling again after correcting the program, the location can be changed.

The benefit of automatic allocation variable is that the user do not need to check the location of internal variable. The variable declared by different name is not duplicated in the data memory.

As the variable location is set for direct variable, it would be better to use %I and %Q. If the user misuse the direct variable, it may be duplicated since it is not automatic allocation variable.

▷	Initial Value allocation : Allocate the initial value of variable. If no, the value of clause 3.2.3. is allocated as initial value.

Reference

The initial value can not be allocated if VAR_EXTERNAL is declared.

The initial value can not be allocated if %I and %Q are allocated.

▷	After PLC is switched off, the variable, which requires the data, can be declared by VAR_RETAIN supplying retention function under below regulation.

1)	Retention variable is retained at the warm restart.

2)	During cold restart of system, it is initialized to initial value defined by user or basic initial value.

▷ Variable not declared by VAR_RETAIN is initialized to initial value defined by user or basic initial value during cold restart or warm restart.

Reference

The variable allocated to %I and %Q can not be declared to VAR_RETAIN,

VAR_CONSTANT.

▷	The variable can be used by declaring basic data type to array. To declare array variable, the type and array size to be used for parameter shall be declared. 
However, string data type in basic data type can not be set to parameter.

▷	Scope of variable declaration, i.e., region to use variable, is restricted to the program configuration element that the variable is declared. Therefore, the variable declared in other program configuration element can not be used. The variable declared as global variable can be accessed in all location by declaring VAR_EXTERNAL.
The configuration global variable can be used all program configuration element of all resources and the resource global variable can be used in all program configuration element.

Example of variable declaration

| Name | Type | Data type | Initial value | Memory allocation |
| --- | --- | --- | --- | --- |
| I_VAL | VAR | INT | 1234 | Automatic |
| BIPOLAR | VAR_RETAIN | REAL |  | Automatic |
| LIMIT_SW | VAR | BOOL |  | %IX1.0.2 |
| GLO_SW | VAR_EXTERNAL | DWORD |  | Automatic |
| READ_BUF | VAR | ARRAY OF INT[10] |  | Automatic |

4.2 Elementary data types

GLOFA PLC supports the basic data type as below.

| No. | Keyword | Data type | Size (Bit) | Range |
| --- | --- | --- | --- | --- |
| 1 | SINT | Short integer | 8 | -128 ~ 127 |
| 2 | INT | Integer | 16 | -32768 ~ 32767 |
| 3 | DINT | Double integer | 32 | -2147483648 ~ 2147483647 |
| 4 | LINT | Long integer | 64 | -263 ~ 263-1 |
| 5 | USINT | Unsigned short integer | 8 | 0 ~ 255 |
| 6 | UINT | Unsigned integer | 16 | 0 ~ 65535 |
| 7 | UDINT | Unsigned double integer | 32 | 0 ~ 4294967295 |
| 8 | ULINT | Unsigned long integer | 64 | 0 ~ 264-1 |
| 9 | REAL | Real numbers | 32 | -3.402823E38 ~ -1.401298E-45 1.401298E-45 ~ 3.402823E38 |
| 10 | LREAL | Long reals | 64 | -1.7976931E308 ~-4.9406564E-324 4.9406564E-324 ~ 1.7976931E308 |
| 11 | TIME | Duration | 32 | T#0S ~ T#49D17H2M47S295MS |
| 12 | DATE | Date | 16 | D#1984-01-01 ~ D#2163-6-6 |
| 13 | TIME_OF_DAY | Time of day | 32 | TOD#00:00:00 ~ TOD#23:59:59.999 |
| 14 | DATE_AND_TIME | Date and time of day | 64 | DT#1984-01-01-00:00:00 ~ DT#2163-12-31-23:59:59.999 |
| 15 | STRING | Character string | 30*8 | - |
| 16 | BOOL | Boolean | 1 | 0,1 |
| 17 | BYTE | Bit string of length 8 | 8 | 16#0 ~ 16#FF |
| 18 | WORD | Bit string of length 16 | 16 | 16#0 ~ 16#FFFF |
| 19 | DWORD | Bit string of length 32 | 32 | 16#0 ~ 16#FFFFFFFF |
| 20 | LWORD | Bit string of length 64 | 64 | 16#0 ~ 16#FFFFFFFFFFFFFFFF |

Note

LINT, ULINT, REAL, LREAL and LWORD is supported in GM1 and GM2.